## Sheet1
| timestamp | elapsed_time_min | elapsed_time_sec | phase | airend_discharge_temp_c | delivery_pressure_kg_cm2g | oil_cooler_inlet_temp_c | oil_cooler_outlet_temp_c | aftercooler_inlet_temp_c | aftercooler_outlet_temp_c | fad_cfm | motor_output_power_kw | package_input_power_kw | input_voltage_v | current_package_input_a | aos_tank_inlet_pressure_kg_cm2g | air_inlet_temp_c | power_factor | tolerance_flow_pct | spc_kw_per_m3_min | tolerance_spc_pct | rated_fad_cfm | flow_tolerance_pct(%) | rated_motor_output_kw | (motor_power_tolerance_pct(%))
0 | 2026-02-14 16:23 | 0 | 77.5914 | Phase1_Warmup | 33.389 | 0.048702 | 35.7888 | 32.4791 | 33.1259 | 32.0357 | 0.095704 | 0.043252 | 0.14372 | 415.2017 | 0.24412 | -0.011253 | 32.5518 | -0.0045674 | -100.1329 | -8.5773 | 213.997 | 127 | 7 | 22 | 5
1 | 2026-02-14 16:23 | 0.22716 | -6.1643 | Phase1_Warmup | 33.8698 | 1.1198 | 36.0696 | 33.2234 | 33.3599 | 32.5346 | 8.3604 | 20.3954 | 22.6848 | 415.6365 | 49.1167 | 1.0573 | 32.3272 | 0.0067778 | -94.0911 | 107.9026 | -1248.8832 | 127 | 7 | 22 | 5
2 | 2026-02-14 16:24 | 0.45432 | 132.0428 | Phase1_Warmup | 35.0177 | 2.163 | 35.6458 | 33.2128 | 33.7262 | 32.7006 | 13.4444 | 15.3042 | 16.5259 | 415.2521 | 35.9492 | 2.0602 | 32.4549 | 0.011094 | -89.1585 | 43.3566 | -437.4339 | 127 | 7 | 22 | 5
3 | 2026-02-14 16:24 | 0.68148 | 284.2132 | Phase1_Warmup | 34.9443 | 2.9999 | 35.9902 | 33.8354 | 33.3699 | 32.5887 | 19.6084 | 11.8713 | 13.4386 | 415.3639 | 27.767 | 2.8243 | 32.5114 | 0.0054131 | -85.0423 | 25.0325 | -213.7228 | 127 | 7 | 22 | 5
4 | 2026-02-14 16:24 | 0.90864 | 25.1587 | Phase1_Warmup | 34.896 | 3.7147 | 35.9672 | 33.4603 | 33.8076 | 32.8071 | 24.8411 | 10.506 | 11.6079 | 415.7628 | 23.806 | 3.4892 | 32.4743 | 0.84384 | -79.5496 | 16.4476 | -107.0021 | 127 | 7 | 22 | 5
5 | 2026-02-14 16:24 | 1.1358 | 40.5952 | Phase1_Warmup | 35.7718 | 4.356 | 36.526 | 33.7521 | 34.1584 | 32.5598 | 29.6489 | 9.6164 | 10.6776 | 416.1215 | 21.5346 | 4.223 | 32.4916 | 0.85716 | -77.5302 | 13.2348 | -59.3519 | 127 | 7 | 22 | 5
6 | 2026-02-14 16:24 | 1.363 | 339.2912 | Phase1_Warmup | 36.1556 | 4.8727 | 36.9927 | 34.0227 | 34.3847 | 33.175 | 33.528 | 9.7239 | 10.8461 | 415.5639 | 21.9312 | 4.654 | 32.5801 | 0.8656 | -73.4643 | 11.3563 | -42.2941 | 127 | 7 | 22 | 5
7 | 2026-02-14 16:25 | 1.5901 | 227.9178 | Phase1_Warmup | 36.1092 | 5.2676 | 37.4115 | 33.7248 | 34.5625 | 33.1248 | 36.859 | 9.8447 | 11.41 | 415.8842 | 22.1186 | 5.1423 | 32.4425 | 0.87241 | -71.2117 | 10.7095 | -35.0229 | 127 | 7 | 22 | 5
8 | 2026-02-14 16:25 | 1.8173 | 50.1351 | Phase1_Warmup | 36.2595 | 5.7023 | 37.2054 | 34.5376 | 34.9374 | 33.4209 | 41.4405 | 10.5292 | 11.9061 | 414.4227 | 22.6491 | 5.6498 | 32.5102 | 0.85058 | -66.3878 | 9.8368 | -21.7531 | 127 | 7 | 22 | 5
9 | 2026-02-14 16:25 | 2.0444 | 223.6582 | Phase1_Warmup | 37.5269 | 6.045 | 37.5896 | 34.6797 | 35.1683 | 33.4716 | 46.8668 | 11.048 | 12.402 | 415.6994 | 23.3772 | 5.8457 | 32.5586 | 0.8644 | -64.2967 | 9.7429 | -19.6499 | 127 | 7 | 22 | 5
10 | 2026-02-14 16:25 | 2.2716 | 81.949 | Phase1_Warmup | 37.3713 | 6.3232 | 37.9639 | 34.9312 | 35.5129 | 33.4511 | 50.7121 | 11.7013 | 13.1673 | 415.4138 | 24.9401 | 6.3062 | 32.4932 | 0.86722 | -60.2647 | 9.257 | -13.1606 | 127 | 7 | 22 | 5
11 | 2026-02-14 16:26 | 2.4988 | 97.0217 | Phase1_Warmup | 38.4734 | 6.6138 | 37.9447 | 35.7528 | 35.4574 | 33.9612 | 54.4959 | 12.5133 | 14.1827 | 415.9482 | 25.9814 | 6.4565 | 32.5606 | 0.86303 | -57.2435 | 8.7703 | -15.3164 | 127 | 7 | 22 | 5
12 | 2026-02-14 16:26 | 2.7259 | 223.0037 | Phase1_Warmup | 37.8943 | 6.7305 | 39.0687 | 34.7635 | 35.8467 | 33.6243 | 58.4561 | 12.9601 | 14.6373 | 416.5248 | 27.575 | 6.6959 | 32.5048 | 0.87073 | -53.5084 | 9.1895 | -12.7341 | 127 | 7 | 22 | 5
13 | 2026-02-14 16:26 | 2.9531 | -98.2313 | Phase1_Warmup | 39.9774 | 6.868 | 38.4676 | 35.7371 | 36.5092 | 34.1921 | 61.8243 | 13.7137 | 15.6856 | 414.6772 | 28.7534 | 6.9232 | 32.4566 | 0.86357 | -51.4827 | 8.7042 | -15.9962 | 127 | 7 | 22 | 5
14 | 2026-02-14 16:26 | 3.1803 | -53.3734 | Phase1_Warmup | 40.3012 | 7.1047 | 39.233 | 35.7317 | 36.8329 | 34.5491 | 66.2881 | 14.3823 | 16.0735 | 416.5681 | 29.6261 | 7.0608 | 32.5756 | 0.86248 | -48.8838 | 9.0396 | -8.9328 | 127 | 7 | 22 | 5
15 | 2026-02-14 16:27 | 3.4074 | 143.6742 | Phase1_Warmup | 41.0429 | 7.2059 | 40.065 | 36.2579 | 36.4021 | 34.8092 | 68.278 | 15.2344 | 17.0187 | 414.7897 | 31.1371 | 7.2352 | 32.4595 | 0.88008 | -45.0737 | 8.6854 | -8.783 | 127 | 7 | 22 | 5
16 | 2026-02-14 16:27 | 3.6346 | 88.729 | Phase1_Warmup | 42.1086 | 7.3131 | 40.101 | 36.2978 | 37.3156 | 35.2556 | 70.3651 | 15.6127 | 17.6597 | 414.668 | 32.1593 | 7.3546 | 32.5801 | 0.85559 | -43.5257 | 8.9918 | -11.9801 | 127 | 7 | 22 | 5
17 | 2026-02-14 16:27 | 3.8617 | 311.4649 | Phase1_Warmup | 43.4833 | 7.4199 | 40.5531 | 36.3927 | 36.8743 | 35.3572 | 75.0674 | 16.2755 | 18.4249 | 415.3135 | 33.051 | 7.5683 | 32.4999 | 0.86818 | -41.7498 | 8.9046 | -7.4475 | 127 | 7 | 22 | 5
18 | 2026-02-14 16:28 | 4.0889 | 135.9687 | Phase1_Warmup | 43.8969 | 7.4789 | 40.8222 | 36.764 | 37.753 | 35.3373 | 77.0417 | 16.7027 | 18.9172 | 415.7713 | 33.8558 | 7.6107 | 32.4811 | 0.86579 | -39.367 | 8.7219 | -4.8259 | 127 | 7 | 22 | 5
19 | 2026-02-14 16:28 | 4.3161 | 72.6294 | Phase1_Warmup | 43.3634 | 7.5294 | 41.4412 | 37.3423 | 38.6119 | 35.6351 | 80.1864 | 17.4014 | 19.2047 | 416.4165 | 34.3866 | 7.7691 | 32.5521 | 0.86536 | -35.7997 | 8.6469 | -6.8524 | 127 | 7 | 22 | 5
20 | 2026-02-14 16:28 | 4.5432 | 537.6263 | Phase1_Warmup | 44.948 | 7.6145 | 42.1974 | 37.24 | 38.394 | 35.8013 | 84.1605 | 17.4639 | 20.0616 | 417.6073 | 35.8349 | 7.8077 | 32.5347 | 0.87407 | -34.9431 | 8.5738 | -4.9109 | 127 | 7 | 22 | 5
21 | 2026-02-14 16:28 | 4.7704 | 288.8439 | Phase1_Warmup | 46.0142 | 7.5967 | 41.6329 | 37.8622 | 38.7242 | 35.832 | 84.8772 | 18.1265 | 20.7077 | 414.5965 | 36.2652 | 7.8527 | 32.4907 | 0.87379 | -33.6068 | 8.1296 | -5.5737 | 127 | 7 | 22 | 5
22 | 2026-02-14 16:28 | 4.9975 | 350.0947 | Phase1_Warmup | 47.3484 | 7.6596 | 43.0907 | 38.096 | 39.4555 | 36.1943 | 87.487 | 18.2395 | 20.9356 | 415.2539 | 36.683 | 7.9314 | 32.4915 | 0.87293 | -31.7531 | 8.4651 | -8.0703 | 127 | 7 | 22 | 5
23 | 2026-02-14 16:29 | 5.2247 | 132.4211 | Phase1_Warmup | 49.0717 | 7.7634 | 42.8822 | 38.3538 | 39.4111 | 36.4728 | 88.6245 | 18.6217 | 21.209 | 415.9221 | 37.884 | 7.9964 | 32.5396 | 0.87931 | -29.803 | 8.1827 | 0.65103 | 127 | 7 | 22 | 5
24 | 2026-02-14 16:29 | 5.4519 | 285.3763 | Phase1_Warmup | 49.287 | 7.7572 | 43.9965 | 38.8655 | 39.8856 | 36.5652 | 91.6732 | 19.3181 | 21.6596 | 414.988 | 38.5407 | 8.002 | 32.409 | 0.87368 | -28.063 | 8.3921 | -5.1189 | 127 | 7 | 22 | 5
25 | 2026-02-14 16:29 | 5.679 | 403.175 | Phase1_Warmup | 51.3913 | 7.8207 | 44.2899 | 39.2708 | 40.621 | 37.1021 | 94.3967 | 19.6526 | 22.2415 | 414.3317 | 38.6537 | 8.0837 | 32.4283 | 0.87229 | -26.9136 | 8.1394 | -2.4321 | 127 | 7 | 22 | 5
26 | 2026-02-14 16:30 | 5.9062 | 221.4859 | Phase1_Warmup | 52.3335 | 7.7484 | 44.9271 | 39.445 | 40.6334 | 37.4051 | 94.6484 | 19.9719 | 22.445 | 415.2897 | 39.5918 | 8.1408 | 32.585 | 0.88022 | -25.1906 | 8.0677 | -1.3417 | 127 | 7 | 22 | 5
27 | 2026-02-14 16:30 | 6.1333 | 475.4032 | Phase1_Warmup | 53.6388 | 7.8285 | 45.1078 | 40.0802 | 41.0562 | 37.4209 | 97.656 | 20.2445 | 23.0554 | 415.532 | 39.6869 | 8.0999 | 32.5413 | 0.86888 | -23.7829 | 8.617 | -3.3672 | 127 | 7 | 22 | 5
28 | 2026-02-14 16:30 | 6.3605 | 338.3243 | Phase1_Warmup | 54.6184 | 7.9231 | 46.1912 | 40.3851 | 41.6378 | 38.0637 | 99.3369 | 20.9706 | 23.2531 | 415.683 | 40.3423 | 8.1102 | 32.5537 | 0.87691 | -21.459 | 8.503 | -1.3919 | 127 | 7 | 22 | 5
29 | 2026-02-14 16:30 | 6.5877 | 402.0183 | Phase1_Warmup | 55.9944 | 7.8393 | 47.1818 | 40.9779 | 42.3676 | 38.5931 | 101.0569 | 20.8516 | 23.2525 | 415.0466 | 40.3331 | 8.1519 | 32.4676 | 0.86996 | -20.7057 | 8.2684 | -2.1212 | 127 | 7 | 22 | 5
30 | 2026-02-14 16:30 | 6.8148 | 369.0253 | Phase1_Warmup | 57.6199 | 7.8583 | 46.8191 | 41.1174 | 42.6857 | 38.5747 | 103.0872 | 21.2042 | 23.7961 | 416.6982 | 40.9619 | 8.1075 | 32.5833 | 0.87117 | -19.6474 | 8.2615 | -5.7921 | 127 | 7 | 22 | 5
31 | 2026-02-14 16:31 | 7.042 | 767.7944 | Phase1_Warmup | 59.2669 | 7.8906 | 47.8032 | 41.9339 | 42.8753 | 38.8761 | 104.3346 | 21.3065 | 23.9845 | 415.6202 | 41.1712 | 8.2449 | 32.4709 | 0.87077 | -17.2315 | 8.1231 | -2.3817 | 127 | 7 | 22 | 5
32 | 2026-02-14 16:31 | 7.2692 | 491.7769 | Phase1_Warmup | 61.5736 | 7.8648 | 48.2148 | 41.7852 | 43.4583 | 39.1522 | 106.6028 | 21.6774 | 24.3435 | 416.0188 | 41.5924 | 8.2411 | 32.6198 | 0.87452 | -16.1813 | 8.2981 | -3.1765 | 127 | 7 | 22 | 5
33 | 2026-02-14 16:31 | 7.4963 | 344.0949 | Phase1_Warmup | 62.4826 | 7.8985 | 48.9251 | 42.3667 | 43.7991 | 39.5881 | 106.0862 | 21.87 | 24.541 | 414.5915 | 41.66 | 8.2179 | 32.5194 | 0.866 | -16.0002 | 8.003 | -2.2816 | 127 | 7 | 22 | 5
34 | 2026-02-14 16:32 | 7.7235 | 653.2423 | Phase1_Warmup | 65.3601 | 7.9087 | 49.481 | 42.6194 | 44.3024 | 39.8467 | 108.1607 | 21.9658 | 24.8551 | 413.5806 | 42.1761 | 8.179 | 32.5542 | 0.87574 | -15.3376 | 8.3134 | -4.023 | 127 | 7 | 22 | 5
35 | 2026-02-14 16:32 | 7.9506 | 349.4799 | Phase1_Warmup | 65.6513 | 7.9868 | 49.9836 | 43.2997 | 44.5675 | 39.9022 | 109.403 | 22.3913 | 25.137 | 416.0425 | 42.5156 | 8.2595 | 32.5774 | 0.8626 | -14.4793 | 8.0411 | 2.416 | 127 | 7 | 22 | 5
36 | 2026-02-14 16:32 | 8.1778 | 588.2474 | Phase1_Warmup | 66.9242 | 7.9168 | 51.0023 | 43.4278 | 45.1151 | 40.3425 | 109.5099 | 22.5429 | 25.2623 | 415.7873 | 42.4739 | 8.2959 | 32.5309 | 0.86997 | -12.6138 | 8.0043 | 3.6786 | 127 | 7 | 22 | 5
37 | 2026-02-14 16:32 | 8.405 | 264.9362 | Phase1_Warmup | 68.0848 | 7.9196 | 51.8979 | 43.8227 | 45.5221 | 40.8241 | 112.7143 | 22.6636 | 25.4169 | 416.078 | 42.7992 | 8.278 | 32.51 | 0.87068 | -12.012 | 8.0607 | 2.5226 | 127 | 7 | 22 | 5
38 | 2026-02-14 16:32 | 8.6321 | 379.0138 | Phase1_Warmup | 70.3394 | 7.9518 | 52.0877 | 44.1977 | 46.0833 | 40.8588 | 114.8551 | 22.4592 | 25.5189 | 415.3454 | 43.1722 | 8.2574 | 32.5844 | 0.86828 | -11.3447 | 7.8843 | 3.9179 | 127 | 7 | 22 | 5
39 | 2026-02-14 16:33 | 8.8593 | 632.6742 | Phase1_Warmup | 71.0488 | 7.9389 | 52.8168 | 44.5126 | 46.149 | 41.6895 | 113.9439 | 22.8247 | 25.805 | 415.0502 | 43.6056 | 8.2467 | 32.5916 | 0.86937 | -10.8037 | 8.0866 | -0.37044 | 127 | 7 | 22 | 5
40 | 2026-02-14 16:33 | 9.0864 | 732.7119 | Phase1_Warmup | 72.6113 | 7.9977 | 52.4477 | 44.9794 | 46.7711 | 41.2443 | 115.0809 | 23.3051 | 25.8496 | 415.3795 | 43.4936 | 8.2745 | 32.5494 | 0.87176 | -10.2229 | 7.9076 | -1.0833 | 127 | 7 | 22 | 5
41 | 2026-02-14 16:33 | 9.3136 | 659.5598 | Phase1_Warmup | 75.0776 | 7.8933 | 53.3623 | 45.3711 | 47.4476 | 41.7319 | 115.8432 | 23.082 | 26.2585 | 416.2275 | 43.502 | 8.2495 | 32.4043 | 0.86843 | -8.6297 | 8.1072 | -1.3513 | 127 | 7 | 22 | 5
42 | 2026-02-14 16:34 | 9.5408 | 630.1591 | Phase1_Warmup | 75.1627 | 7.9544 | 54.3306 | 45.5521 | 47.7672 | 41.9582 | 116.3358 | 23.3619 | 26.1623 | 415.0888 | 43.7932 | 8.2559 | 32.5811 | 0.86972 | -8.7931 | 8.1576 | 3.5869 | 127 | 7 | 22 | 5
43 | 2026-02-14 16:34 | 9.7679 | 616.6231 | Phase1_Warmup | 76.7153 | 7.9631 | 55.0272 | 46.0359 | 48.2702 | 42.325 | 116.3521 | 23.6782 | 26.5402 | 415.4504 | 44.0797 | 8.3468 | 32.5876 | 0.85866 | -6.5335 | 7.7693 | 2.4273 | 127 | 7 | 22 | 5
44 | 2026-02-14 16:34 | 9.9951 | 448.1334 | Phase1_Warmup | 76.8157 | 7.9456 | 54.9663 | 46.6894 | 48.4322 | 42.3213 | 117.9722 | 23.5057 | 26.6264 | 415.6159 | 43.9106 | 8.4246 | 32.5689 | 0.88229 | -6.9956 | 7.8815 | 1.7691 | 127 | 7 | 22 | 5
45 | 2026-02-14 16:34 | 10.2222 | 582.0798 | Phase1_Warmup | 78.6088 | 7.879 | 55.4447 | 46.6638 | 48.9513 | 42.7482 | 117.9203 | 23.4689 | 26.5883 | 416.074 | 43.9451 | 8.2523 | 32.4269 | 0.86321 | -6.3322 | 8.0329 | 4.9186 | 127 | 7 | 22 | 5
46 | 2026-02-14 16:35 | 10.4494 | 638.004 | Phase1_Warmup | 80.3621 | 7.9309 | 55.9406 | 47.1977 | 49.2528 | 42.8124 | 121.5217 | 23.4214 | 26.7609 | 417.2808 | 44.3657 | 8.3065 | 32.5194 | 0.86804 | -6.3129 | 7.7754 | 3.5727 | 127 | 7 | 22 | 5
47 | 2026-02-14 16:35 | 10.6766 | 890.5263 | Phase1_Warmup | 80.0987 | 7.9412 | 56.1927 | 47.1489 | 49.8394 | 43.2504 | 120.7603 | 23.9159 | 26.6664 | 415.2104 | 44.4601 | 8.2569 | 32.4025 | 0.88506 | -4.8453 | 7.9515 | 0.51272 | 127 | 7 | 22 | 5
48 | 2026-02-14 16:35 | 10.9037 | 794.5043 | Phase1_Warmup | 82.2747 | 7.9329 | 57.2261 | 47.4801 | 49.8073 | 43.5243 | 120.9436 | 23.7574 | 27.0217 | 417.4619 | 44.1391 | 8.3692 | 32.5592 | 0.87564 | -4.7572 | 7.9873 | 0.71634 | 127 | 7 | 22 | 5
49 | 2026-02-14 16:35 | 11.1309 | 480.8586 | Phase1_Warmup | 82.3472 | 7.994 | 57.6576 | 47.7631 | 50.2947 | 43.7358 | 122.718 | 23.9694 | 26.9752 | 416.0366 | 44.3282 | 8.2506 | 32.5206 | 0.87017 | -3.9894 | 8.0807 | 4.4017 | 127 | 7 | 22 | 5
50 | 2026-02-14 16:36 | 11.358 | 822.3207 | Phase1_Warmup | 82.4656 | 7.8981 | 57.4916 | 48.2252 | 50.5358 | 43.4642 | 121.7902 | 23.9088 | 26.991 | 415.8542 | 44.6823 | 8.2641 | 32.5265 | 0.86918 | -2.3972 | 7.7106 | 5.632 | 127 | 7 | 22 | 5
51 | 2026-02-14 16:36 | 11.5852 | 726.9762 | Phase1_Warmup | 83.9839 | 7.9705 | 58.0885 | 48.5607 | 50.7322 | 44.5808 | 122.8187 | 24.1322 | 27.1539 | 415.1865 | 44.8223 | 8.3705 | 32.4868 | 0.87177 | -2.6711 | 7.5937 | 4.9895 | 127 | 7 | 22 | 5
52 | 2026-02-14 16:36 | 11.8124 | 696.8221 | Phase1_Warmup | 84.6423 | 7.9577 | 58.5619 | 48.3937 | 50.7739 | 44.4448 | 123.8692 | 24.1538 | 27.0109 | 416.3294 | 45.1417 | 8.3328 | 32.5269 | 0.85879 | -3.0324 | 7.7718 | 7.8486 | 127 | 7 | 22 | 5
53 | 2026-02-14 16:36 | 12.0395 | 913.547 | Phase1_Warmup | 85.2242 | 7.997 | 58.8371 | 48.584 | 51.4776 | 44.3302 | 124.884 | 24.3039 | 27.0705 | 417.0908 | 44.7384 | 8.3215 | 32.4745 | 0.86639 | -2.8098 | 7.6063 | 7.5688 | 127 | 7 | 22 | 5
54 | 2026-02-14 16:36 | 12.2667 | 994.4831 | Phase1_Warmup | 84.5949 | 7.9821 | 59.1159 | 48.7116 | 52.21 | 44.7552 | 125.2137 | 24.2698 | 27.4033 | 414.8044 | 44.7715 | 8.3081 | 32.4064 | 0.85128 | -1.3452 | 7.9091 | 4.6708 | 127 | 7 | 22 | 5
55 | 2026-02-14 16:37 | 12.4939 | 994.3399 | Phase1_Warmup | 85.4001 | 7.9904 | 60.0821 | 49.1744 | 51.7542 | 44.9327 | 125.7379 | 24.4844 | 27.5292 | 415.3578 | 44.9142 | 8.2951 | 32.4662 | 0.87122 | -0.30283 | 7.5361 | 1.6498 | 127 | 7 | 22 | 5
56 | 2026-02-14 16:37 | 12.721 | 733.2056 | Phase1_Warmup | 86.4641 | 7.9817 | 59.7111 | 49.5719 | 52.0272 | 44.9455 | 125.8419 | 24.3229 | 27.4644 | 415.4747 | 45.1461 | 8.3767 | 32.5593 | 0.87141 | -0.77841 | 8.2365 | 0.66004 | 127 | 7 | 22 | 5
57 | 2026-02-14 16:37 | 12.9482 | 831.4313 | Phase1_Warmup | 86.6667 | 7.896 | 59.9465 | 49.5131 | 52.373 | 45.2282 | 126.519 | 24.3102 | 27.4102 | 415.1163 | 45.1899 | 8.274 | 32.4611 | 0.86245 | -0.18917 | 8.0285 | 2.9761 | 127 | 7 | 22 | 5
58 | 2026-02-14 16:38 | 13.1753 | 946.9135 | Phase1_Warmup | 87.6719 | 7.9877 | 60.3444 | 50.0908 | 52.6604 | 45.2621 | 126.7365 | 24.5555 | 27.4592 | 414.7767 | 45.2702 | 8.3504 | 32.5363 | 0.86944 | 0.060743 | 7.7285 | 6.3678 | 127 | 7 | 22 | 5
59 | 2026-02-14 16:38 | 13.4025 | 1062.9902 | Phase1_Warmup | 87.7978 | 7.9097 | 60.9046 | 50.0198 | 53.0994 | 45.6627 | 126.164 | 24.5739 | 27.7395 | 415.7653 | 45.4651 | 8.2962 | 32.4325 | 0.85788 | 0.95161 | 7.9108 | 9.0397 | 127 | 7 | 22 | 5
60 | 2026-02-14 16:38 | 13.6297 | 851.1834 | Phase1_Warmup | 87.5398 | 7.9805 | 60.837 | 50.4144 | 52.913 | 45.4751 | 127.4869 | 24.6467 | 27.7916 | 415.8864 | 45.276 | 8.2578 | 32.4531 | 0.86869 | -0.92806 | 7.3798 | 5.6681 | 127 | 7 | 22 | 5
61 | 2026-02-14 16:38 | 13.8568 | 912.4671 | Phase1_Warmup | 88.3951 | 7.9709 | 60.7202 | 50.4069 | 53.3228 | 45.4996 | 127.0624 | 24.849 | 27.7076 | 415.8251 | 45.447 | 8.2767 | 32.4594 | 0.87596 | 1.194 | 8.201 | 7.9999 | 127 | 7 | 22 | 5
62 | 2026-02-14 16:39 | 14.084 | 784.0829 | Phase1_Warmup | 88.8944 | 7.9683 | 61.5542 | 50.59 | 53.434 | 46.173 | 128.0213 | 24.7109 | 27.9474 | 415.283 | 45.503 | 8.3131 | 32.3812 | 0.87201 | 1.3979 | 7.5875 | 4.0871 | 127 | 7 | 22 | 5
63 | 2026-02-14 16:39 | 14.3111 | 785.478 | Phase1_Warmup | 89.2024 | 7.8609 | 61.8687 | 50.1378 | 53.6141 | 46.2602 | 127.895 | 24.7311 | 27.8709 | 415.7032 | 45.2298 | 8.3527 | 32.5355 | 0.87035 | 0.14099 | 7.6702 | 6.4916 | 127 | 7 | 22 | 5
64 | 2026-02-14 16:39 | 14.5383 | 1114.6946 | Phase1_Warmup | 89.761 | 8.0179 | 61.5758 | 50.6672 | 53.8987 | 46.3382 | 130.7219 | 24.6814 | 27.862 | 416.5573 | 45.5333 | 8.3281 | 32.628 | 0.8681 | 0.67864 | 7.3354 | 6.7568 | 127 | 7 | 22 | 5
65 | 2026-02-14 16:39 | 14.7655 | 1215.0618 | Phase1_Warmup | 89.959 | 7.975 | 61.1334 | 50.4773 | 53.9777 | 46.5835 | 129.2493 | 24.8316 | 27.867 | 415.8148 | 45.5367 | 8.3678 | 32.5037 | 0.872 | 1.2384 | 7.7604 | 0.28918 | 127 | 7 | 22 | 5
66 | 2026-02-14 16:40 | 14.9926 | 1007.3897 | Phase1_Warmup | 89.8834 | 7.9087 | 62.3886 | 51.33 | 54.2973 | 46.5129 | 128.3349 | 24.8696 | 27.7163 | 416.1915 | 45.298 | 8.3324 | 32.4943 | 0.87457 | 1.4954 | 7.4201 | 4.4814 | 127 | 7 | 22 | 5
67 | 2026-02-14 16:40 | 15.2198 | 1190.8335 | Phase1_Warmup | 89.7513 | 7.9985 | 61.8501 | 51.3192 | 54.049 | 46.5174 | 129.5136 | 24.785 | 27.9871 | 415.4042 | 45.7142 | 8.3046 | 32.4437 | 0.86036 | 1.7507 | 7.6892 | 7.7153 | 127 | 7 | 22 | 5
68 | 2026-02-14 16:40 | 15.4469 | 1105.9971 | Phase1_Warmup | 89.2429 | 7.9509 | 62.389 | 51.5084 | 54.4603 | 46.725 | 130.7305 | 24.7017 | 28.1694 | 416.2063 | 45.8626 | 8.3203 | 32.5562 | 0.87753 | 2.7557 | 7.5242 | 6.4082 | 127 | 7 | 22 | 5
69 | 2026-02-14 16:40 | 15.6741 | 964.1664 | Phase1_Warmup | 90.6453 | 7.8935 | 62.0452 | 51.8538 | 54.4405 | 46.4745 | 131.9462 | 25.0917 | 28.295 | 416.2163 | 45.4021 | 8.2819 | 32.605 | 0.85979 | 3.3641 | 7.4499 | 2.2227 | 127 | 7 | 22 | 5
70 | 2026-02-14 16:40 | 15.9013 | 1136.8274 | Phase1_Warmup | 90.1523 | 7.9566 | 62.7563 | 51.3514 | 54.6498 | 46.8826 | 130.2341 | 24.8683 | 28.3744 | 414.9881 | 45.4927 | 8.3457 | 32.5331 | 0.85762 | 3.6447 | 7.4923 | -0.74871 | 127 | 7 | 22 | 5
71 | 2026-02-14 16:41 | 16.1284 | 1336.0636 | Phase1_Warmup | 90.515 | 7.8822 | 62.4176 | 52.0279 | 54.7435 | 46.9427 | 129.5272 | 24.9067 | 28.0924 | 415.6718 | 45.4511 | 8.3335 | 32.5461 | 0.87606 | 2.4799 | 7.681 | 4.8278 | 127 | 7 | 22 | 5
72 | 2026-02-14 16:41 | 16.3556 | 1105.6455 | Phase1_Warmup | 89.9406 | 7.9274 | 63.1387 | 51.835 | 54.7178 | 47.2611 | 131.3789 | 25.0386 | 28.2812 | 415.328 | 45.5503 | 8.2895 | 32.5127 | 0.87406 | 2.3562 | 7.3743 | 5.5665 | 127 | 7 | 22 | 5
73 | 2026-02-14 16:41 | 16.5828 | 1371.0877 | Phase2_Stabilization | 91.1139 | 7.9322 | 64.7182 | 53.2204 | 56.7186 | 48.8432 | 134.6929 | 25.2505 | 28.6698 | 415.6791 | 46.1778 | 8.3194 | 32.5254 | 0.86673 | 7.8303 | 7.3492 | 5.1767 | 127 | 7 | 22 | 5
74 | 2026-02-14 16:41 | 16.8099 | 732.8812 | Phase2_Stabilization | 92.4831 | 7.9697 | 64.244 | 53.2816 | 56.4924 | 48.8762 | 135.4633 | 25.2322 | 28.7811 | 415.637 | 45.9524 | 8.449 | 32.4838 | 0.87133 | 7.3763 | 7.6127 | 8.1428 | 127 | 7 | 22 | 5
75 | 2026-02-14 16:42 | 17.0371 | 1285.9324 | Phase2_Stabilization | 91.7008 | 7.9753 | 64.4488 | 53.0455 | 56.2919 | 48.9482 | 135.3776 | 25.1163 | 28.4802 | 415.4591 | 45.8085 | 8.3762 | 32.5059 | 0.87371 | 6.8204 | 7.9962 | 9.2622 | 127 | 7 | 22 | 5
76 | 2026-02-14 16:42 | 17.2642 | 1186.5751 | Phase2_Stabilization | 92.0225 | 7.9296 | 64.7377 | 53.1648 | 56.3655 | 48.5828 | 135.4149 | 25.4084 | 28.6857 | 415.7161 | 46.0695 | 8.3645 | 32.49 | 0.8731 | 6.9829 | 7.5965 | 9.2476 | 127 | 7 | 22 | 5
77 | 2026-02-14 16:42 | 17.4914 | 1141.7037 | Phase2_Stabilization | 92.0091 | 8.0384 | 64.6952 | 52.8833 | 56.4349 | 48.7759 | 136.4391 | 25.271 | 28.6735 | 415.2682 | 45.773 | 8.3411 | 32.5132 | 0.87493 | 6.96 | 7.2604 | 2.1458 | 127 | 7 | 22 | 5
78 | 2026-02-14 16:42 | 17.7186 | 1218.1792 | Phase2_Stabilization | 91.5032 | 8.0315 | 64.8144 | 53.0163 | 56.7927 | 48.6239 | 135.1103 | 25.7306 | 28.6112 | 416.1015 | 46.0859 | 8.3564 | 32.4536 | 0.88237 | 7.1803 | 7.4244 | 4.1864 | 127 | 7 | 22 | 5
79 | 2026-02-14 16:43 | 17.9457 | 908.8025 | Phase2_Stabilization | 92.3565 | 7.9634 | 65.2826 | 53.0623 | 56.6719 | 48.8432 | 135.8155 | 25.3236 | 28.6202 | 414.6722 | 45.7935 | 8.3248 | 32.569 | 0.87176 | 6.9003 | 7.4751 | 7.1701 | 127 | 7 | 22 | 5
80 | 2026-02-14 16:43 | 18.1729 | 1200.3984 | Phase2_Stabilization | 92.0571 | 7.9817 | 64.2411 | 53.4818 | 56.3711 | 48.6755 | 135.464 | 25.2299 | 28.6762 | 415.1124 | 45.972 | 8.3313 | 32.5933 | 0.87018 | 6.8508 | 7.4069 | 9.303 | 127 | 7 | 22 | 5
81 | 2026-02-14 16:43 | 18.4 | 1305.9314 | Phase2_Stabilization | 92.0531 | 7.8955 | 65.1582 | 53.1864 | 56.9532 | 48.6169 | 135.7545 | 25.3345 | 28.5182 | 413.6292 | 45.7088 | 8.2636 | 32.4265 | 0.87138 | 5.8019 | 7.6631 | 9.113 | 127 | 7 | 22 | 5
82 | 2026-02-14 16:44 | 18.6272 | 1496.4418 | Phase2_Stabilization | 91.836 | 7.9663 | 64.6035 | 53.1608 | 56.6645 | 48.7156 | 135.7297 | 25.3408 | 28.278 | 414.654 | 45.7115 | 8.2939 | 32.3831 | 0.87208 | 6.3576 | 7.4999 | 9.3647 | 127 | 7 | 22 | 5
83 | 2026-02-14 16:44 | 18.8544 | 1200.0563 | Phase2_Stabilization | 91.6739 | 7.959 | 64.3108 | 53.234 | 56.9577 | 48.9108 | 136.0139 | 25.3424 | 28.9384 | 415.9674 | 45.7348 | 8.2936 | 32.4878 | 0.87362 | 6.3655 | 7.6962 | 6.508 | 127 | 7 | 22 | 5
84 | 2026-02-14 16:44 | 19.0815 | 1170.1546 | Phase2_Stabilization | 91.8945 | 7.9987 | 64.0429 | 52.8796 | 56.3367 | 48.5169 | 136.3449 | 25.4204 | 28.5092 | 415.3795 | 46.054 | 8.3015 | 32.5034 | 0.87363 | 6.5573 | 7.4238 | 6.9368 | 127 | 7 | 22 | 5
85 | 2026-02-14 16:44 | 19.3087 | 1233.5036 | Phase2_Stabilization | 92.1655 | 8.0235 | 64.4558 | 53.2674 | 56.5864 | 48.6666 | 135.9603 | 25.2522 | 28.6218 | 415.712 | 45.6492 | 8.2878 | 32.5958 | 0.87628 | 6.1881 | 7.769 | 5.8149 | 127 | 7 | 22 | 5
86 | 2026-02-14 16:44 | 19.5358 | 1470.311 | Phase2_Stabilization | 92.1102 | 7.9253 | 64.6314 | 52.9028 | 56.6792 | 48.5771 | 135.938 | 25.2596 | 28.7857 | 414.6693 | 45.5825 | 8.4157 | 32.4831 | 0.86128 | 6.3893 | 7.4765 | 9.4891 | 127 | 7 | 22 | 5
87 | 2026-02-14 16:45 | 19.763 | 1394.1046 | Phase2_Stabilization | 92.5883 | 7.9432 | 64.4451 | 53.2426 | 56.5008 | 48.2993 | 133.8 | 25.2423 | 28.4628 | 414.1778 | 46.1272 | 8.2886 | 32.5743 | 0.87021 | 5.3993 | 7.3122 | 5.1756 | 127 | 7 | 22 | 5
88 | 2026-02-14 16:45 | 19.9902 | 1275.431 | Phase2_Stabilization | 91.2086 | 7.9236 | 65.1686 | 52.9846 | 56.6206 | 48.8107 | 135.752 | 25.0943 | 28.4013 | 414.5788 | 46.0246 | 8.3454 | 32.425 | 0.87027 | 7.2194 | 7.9235 | 10.1466 | 127 | 7 | 22 | 5
89 | 2026-02-14 16:45 | 20.2173 | 1453.7956 | Phase2_Stabilization | 92.0524 | 7.8899 | 64.2068 | 53.5632 | 56.4961 | 48.8979 | 136.1756 | 25.2631 | 28.5704 | 415.7097 | 45.4299 | 8.393 | 32.4904 | 0.8724 | 6.8553 | 7.101 | 8.5411 | 127 | 7 | 22 | 5
90 | 2026-02-14 16:46 | 20.4445 | 1404.2167 | Phase2_Stabilization | 92.0883 | 7.9878 | 64.5739 | 53.3327 | 56.3039 | 48.8647 | 136.3679 | 25.2924 | 28.3448 | 415.116 | 45.5855 | 8.3349 | 32.506 | 0.87187 | 5.7764 | 7.3361 | 7.7543 | 127 | 7 | 22 | 5
91 | 2026-02-14 16:46 | 20.6717 | 1555.7976 | Phase2_Stabilization | 92.7286 | 8.0026 | 64.2135 | 53.0197 | 56.164 | 48.3828 | 134.9254 | 25.3046 | 28.4793 | 416.8618 | 45.5301 | 8.4053 | 32.4673 | 0.87744 | 6.1464 | 7.3575 | 6.2228 | 127 | 7 | 22 | 5
92 | 2026-02-14 16:46 | 20.8988 | 1310.2529 | Phase2_Stabilization | 91.8993 | 7.9158 | 64.6038 | 53.5102 | 56.4352 | 48.6054 | 135.299 | 25.5006 | 28.5746 | 416.9782 | 45.6517 | 8.4328 | 32.4207 | 0.8656 | 7.1893 | 7.9886 | 4.5953 | 127 | 7 | 22 | 5
93 | 2026-02-14 16:46 | 21.126 | 1384.1702 | Phase2_Stabilization | 92.4365 | 7.9627 | 64.7932 | 53.1777 | 56.5977 | 48.3048 | 135.6427 | 25.4845 | 28.5411 | 416.2835 | 45.2605 | 8.3707 | 32.5818 | 0.87063 | 6.8259 | 7.8392 | 6.4891 | 127 | 7 | 22 | 5
94 | 2026-02-14 16:46 | 21.3531 | 1389.537 | Phase2_Stabilization | 91.3398 | 7.9862 | 64.5665 | 53.1463 | 56.3273 | 48.8704 | 136.4178 | 25.2852 | 28.367 | 414.9599 | 45.8318 | 8.2902 | 32.4679 | 0.8679 | 6.6045 | 7.7821 | 7.2298 | 127 | 7 | 22 | 5
95 | 2026-02-14 16:47 | 21.5803 | 1237.6073 | Phase2_Stabilization | 92.0883 | 8.0138 | 63.719 | 53.2521 | 56.7515 | 48.4327 | 136.3335 | 25.1471 | 28.738 | 415.183 | 45.6028 | 8.3012 | 32.5366 | 0.8801 | 6.6204 | 7.4258 | 1.8052 | 127 | 7 | 22 | 5
96 | 2026-02-14 16:47 | 21.8075 | 1527.9126 | Phase2_Stabilization | 92.4878 | 7.9203 | 64.5289 | 53.2111 | 56.7039 | 49.0137 | 135.292 | 25.2696 | 28.5147 | 415.3374 | 45.9327 | 8.2757 | 32.3981 | 0.86366 | 7.0232 | 7.9753 | 7.5703 | 127 | 7 | 22 | 5
97 | 2026-02-14 16:47 | 22.0346 | 1537.869 | Phase2_Stabilization | 91.6901 | 7.8646 | 64.5575 | 53.3346 | 56.2681 | 48.8696 | 136.3346 | 25.3349 | 28.7161 | 415.3383 | 45.4536 | 8.2583 | 32.6001 | 0.87561 | 5.8089 | 7.5644 | 10.3177 | 127 | 7 | 22 | 5
98 | 2026-02-14 16:48 | 22.2618 | 1513.3224 | Phase2_Stabilization | 92.4592 | 7.9721 | 64.6154 | 53.2562 | 56.2649 | 48.6333 | 135.9742 | 25.2708 | 28.5605 | 415.1258 | 45.7169 | 8.3671 | 32.6505 | 0.87606 | 7.3466 | 7.6907 | 9.4002 | 127 | 7 | 22 | 5
99 | 2026-02-14 16:48 | 22.4889 | 1491.3129 | Phase2_Stabilization | 91.8119 | 7.9837 | 65.1969 | 53.0455 | 56.3571 | 48.6079 | 135.6138 | 25.3383 | 28.5167 | 415.4132 | 45.7299 | 8.3157 | 32.5654 | 0.87073 | 6.3377 | 7.5458 | 6.4612 | 127 | 7 | 22 | 5
100 | 2026-02-14 16:48 | 22.7161 | 1322.2974 | Phase2_Stabilization | 92.636 | 8.0154 | 64.4767 | 52.9144 | 56.4476 | 48.6946 | 135.5398 | 25.3219 | 28.6566 | 415.2586 | 46.0801 | 8.3255 | 32.4902 | 0.86912 | 6.8518 | 7.4968 | 7.8886 | 127 | 7 | 22 | 5
101 | 2026-02-14 16:48 | 22.9433 | 1493.1167 | Phase2_Stabilization | 92.9644 | 7.9476 | 64.9639 | 52.956 | 56.3642 | 48.5189 | 136.6168 | 25.3477 | 28.5159 | 415.3872 | 45.9393 | 8.2782 | 32.4106 | 0.87104 | 7.0581 | 7.4206 | 6.794 | 127 | 7 | 22 | 5
102 | 2026-02-14 16:48 | 23.1704 | 1520.7241 | Phase2_Stabilization | 91.8696 | 7.9837 | 64.7053 | 53.1852 | 56.7538 | 48.602 | 136.1726 | 25.2976 | 28.4403 | 414.1137 | 45.957 | 8.3371 | 32.5393 | 0.8833 | 6.6618 | 7.448 | 8.3773 | 127 | 7 | 22 | 5
103 | 2026-02-14 16:49 | 23.3976 | 1464.37 | Phase2_Stabilization | 91.795 | 7.9861 | 63.8811 | 53.3107 | 56.6006 | 48.5819 | 137.6055 | 25.3312 | 28.772 | 414.8116 | 45.7457 | 8.3797 | 32.5244 | 0.87306 | 6.1821 | 7.6233 | 11.8553 | 127 | 7 | 22 | 5
104 | 2026-02-14 16:49 | 23.6247 | 1579.9328 | Phase2_Stabilization | 92.5437 | 7.8964 | 64.7339 | 52.9845 | 56.32 | 48.3092 | 135.285 | 25.4343 | 28.5589 | 415.907 | 46.034 | 8.2675 | 32.6054 | 0.87951 | 6.8961 | 7.5742 | 10.4043 | 127 | 7 | 22 | 5
105 | 2026-02-14 16:49 | 23.8519 | 1683.6775 | Phase2_Stabilization | 92.5469 | 7.9326 | 64.2831 | 53.5213 | 56.1185 | 48.5072 | 135.9373 | 25.304 | 28.2761 | 416.2125 | 45.4817 | 8.2823 | 32.3881 | 0.87554 | 7.7652 | 7.4878 | 9.3312 | 127 | 7 | 22 | 5
106 | 2026-02-14 16:50 | 24.0791 | 1930.6347 | Phase2_Stabilization | 91.7341 | 7.9561 | 64.545 | 53.5699 | 56.0921 | 48.7111 | 135.5071 | 25.4966 | 28.7969 | 414.3639 | 45.622 | 8.3611 | 32.5204 | 0.87109 | 6.1514 | 7.8079 | 6.7014 | 127 | 7 | 22 | 5
107 | 2026-02-14 16:50 | 24.3062 | 1678.6996 | Phase2_Stabilization | 91.492 | 7.9371 | 64.4558 | 53.2638 | 56.4571 | 48.4858 | 134.7757 | 25.1894 | 28.5144 | 415.933 | 45.8428 | 8.4014 | 32.538 | 0.86855 | 7.8069 | 6.9039 | 9.7206 | 127 | 7 | 22 | 5
108 | 2026-02-14 16:50 | 24.5334 | 1707.0946 | Phase2_Stabilization | 91.6015 | 7.8954 | 64.53 | 53.1743 | 55.9986 | 48.5686 | 136.0716 | 25.123 | 28.4718 | 415.6324 | 46.0841 | 8.348 | 32.441 | 0.87825 | 6.9795 | 7.5781 | 3.9845 | 127 | 7 | 22 | 5
109 | 2026-02-14 16:50 | 24.7605 | 1670.6676 | Phase2_Stabilization | 91.3229 | 8.0163 | 64.3243 | 53.0276 | 56.7625 | 48.8562 | 135.9436 | 25.36 | 28.463 | 414.2632 | 45.8063 | 8.3386 | 32.4114 | 0.87736 | 6.9753 | 7.6721 | 7.027 | 127 | 7 | 22 | 5
110 | 2026-02-14 16:50 | 24.9877 | 1398.0007 | Phase2_Stabilization | 91.2829 | 7.9101 | 64.4836 | 52.9644 | 56.2009 | 48.8816 | 138.0912 | 25.2154 | 28.8863 | 415.7372 | 45.7514 | 8.2936 | 32.6111 | 0.87549 | 6.1005 | 7.7613 | 9.1647 | 127 | 7 | 22 | 5
111 | 2026-02-14 16:51 | 25.2149 | 1709.0228 | Phase2_Stabilization | 91.1169 | 7.9732 | 64.5667 | 53.11 | 57.0012 | 48.4388 | 135.5326 | 25.4607 | 28.3064 | 415.8832 | 45.7003 | 8.3459 | 32.4931 | 0.86966 | 6.3327 | 7.4637 | 10.1926 | 127 | 7 | 22 | 5
112 | 2026-02-14 16:51 | 25.442 | 1738.007 | Phase2_Stabilization | 91.0003 | 7.9311 | 64.2438 | 53.1095 | 56.9765 | 48.8022 | 134.6323 | 25.0821 | 28.5737 | 415.4349 | 45.9278 | 8.3462 | 32.4943 | 0.87781 | 6.4219 | 7.5501 | 9.6463 | 127 | 7 | 22 | 5
113 | 2026-02-14 16:51 | 25.6692 | 2128.8137 | Phase2_Stabilization | 91.6663 | 7.9579 | 64.5718 | 52.8337 | 56.3796 | 48.777 | 135.8948 | 25.5602 | 28.7185 | 416.9556 | 45.9971 | 8.2966 | 32.5945 | 0.86544 | 6.1369 | 7.7139 | 8.6481 | 127 | 7 | 22 | 5
114 | 2026-02-14 16:52 | 25.8964 | 1729.4177 | Phase2_Stabilization | 91.7717 | 7.9353 | 64.0891 | 53.3215 | 56.5145 | 48.39 | 134.0733 | 25.4034 | 28.6748 | 415.1402 | 45.7888 | 8.329 | 32.5235 | 0.87446 | 6.7958 | 7.8158 | 7.4284 | 127 | 7 | 22 | 5
115 | 2026-02-14 16:52 | 26.1235 | 1822.0047 | Phase2_Stabilization | 92.3612 | 7.9716 | 64.8407 | 53.2179 | 56.6784 | 48.6277 | 135.5809 | 25.2188 | 28.4855 | 415.8293 | 45.76 | 8.3594 | 32.4463 | 0.86731 | 6.5494 | 7.4242 | 9.6222 | 127 | 7 | 22 | 5
116 | 2026-02-14 16:52 | 26.3507 | 1784.9118 | Phase2_Stabilization | 91.2531 | 7.99 | 64.52 | 52.6869 | 56.7611 | 48.6898 | 135.8929 | 25.2079 | 28.3607 | 416.0899 | 45.6522 | 8.3199 | 32.4734 | 0.86504 | 8.2085 | 7.5524 | 5.6759 | 127 | 7 | 22 | 5
117 | 2026-02-14 16:52 | 26.5778 | 1623.2096 | Phase2_Stabilization | 91.9394 | 7.9983 | 64.2231 | 52.897 | 56.072 | 48.7442 | 136.3958 | 25.5891 | 28.4654 | 415.9753 | 45.507 | 8.3433 | 32.4817 | 0.87355 | 6.1092 | 7.8474 | 5.8967 | 127 | 7 | 22 | 5
118 | 2026-02-14 16:52 | 26.805 | 1999.7215 | Phase2_Stabilization | 91.2602 | 7.9358 | 64.1726 | 53.0773 | 56.1935 | 48.3891 | 136.4172 | 25.2421 | 28.5411 | 414.9505 | 45.7521 | 8.3492 | 32.5363 | 0.86832 | 6.843 | 7.0611 | 8.3113 | 127 | 7 | 22 | 5
119 | 2026-02-14 16:53 | 27.0322 | 1954.0948 | Phase2_Stabilization | 91.4553 | 7.9724 | 64.8476 | 53.402 | 56.195 | 48.5826 | 135.3842 | 25.2504 | 28.4992 | 415.8701 | 45.5768 | 8.3815 | 32.494 | 0.87781 | 7.0952 | 7.367 | 8.4626 | 127 | 7 | 22 | 5
120 | 2026-02-14 16:53 | 27.2593 | 1975.6363 | Phase2_Stabilization | 91.9327 | 7.9289 | 64.0844 | 53.1679 | 56.4991 | 48.527 | 135.462 | 25.0566 | 28.5566 | 416.237 | 45.5255 | 8.2641 | 32.5334 | 0.86469 | 6.0585 | 7.8028 | 3.4418 | 127 | 7 | 22 | 5
121 | 2026-02-14 16:53 | 27.4865 | 1725.4489 | Phase2_Stabilization | 90.7676 | 7.9375 | 64.491 | 52.9388 | 56.3342 | 48.6162 | 134.9525 | 25.2512 | 28.6453 | 417.5035 | 45.7532 | 8.3676 | 32.4556 | 0.87027 | 7.2175 | 7.7335 | 9.201 | 127 | 7 | 22 | 5
122 | 2026-02-14 16:54 | 27.7136 | 2102.0671 | Phase2_Stabilization | 91.5924 | 7.9903 | 64.7594 | 53.4133 | 56.5597 | 48.8169 | 134.4523 | 25.2796 | 28.6311 | 416.9569 | 45.6534 | 8.3636 | 32.5054 | 0.87949 | 6.3479 | 7.6148 | 10.0494 | 127 | 7 | 22 | 5
123 | 2026-02-14 16:54 | 27.9408 | 1679.3893 | Phase2_Stabilization | 91.5234 | 7.9164 | 64.7567 | 52.8867 | 56.1274 | 48.9084 | 136.0855 | 25.4303 | 28.4236 | 415.7411 | 45.6609 | 8.2818 | 32.5047 | 0.87385 | 5.3122 | 7.413 | 7.9233 | 127 | 7 | 22 | 5
124 | 2026-02-14 16:54 | 28.168 | 2005.478 | Phase2_Stabilization | 91.8065 | 7.9226 | 64.3823 | 53.3513 | 55.8425 | 48.5494 | 134.2989 | 25.1747 | 28.8726 | 416.6678 | 46.1014 | 8.3045 | 32.5486 | 0.87745 | 7.0182 | 7.3508 | 13.8758 | 127 | 7 | 22 | 5
125 | 2026-02-14 16:54 | 28.3951 | 2271.4089 | Phase2_Stabilization | 91.5952 | 7.9728 | 64.2408 | 53.0679 | 56.5707 | 48.3564 | 135.7838 | 25.1401 | 28.6415 | 414.8414 | 45.7884 | 8.4041 | 32.4532 | 0.86601 | 6.455 | 7.3573 | 6.7323 | 127 | 7 | 22 | 5
126 | 2026-02-14 16:55 | 28.6223 | 1789.9423 | Phase2_Stabilization | 92.971 | 7.9319 | 64.8422 | 53.1338 | 56.0496 | 48.85 | 134.8941 | 25.3744 | 28.5118 | 415.75 | 45.7687 | 8.3635 | 32.6144 | 0.86819 | 6.1813 | 7.8111 | 7.3816 | 127 | 7 | 22 | 5
127 | 2026-02-14 16:55 | 28.8494 | 1871.6462 | Phase2_Stabilization | 90.8807 | 7.9776 | 64.7952 | 53.3442 | 55.8917 | 48.7451 | 136.3738 | 25.5064 | 28.7011 | 416.5678 | 45.8353 | 8.3762 | 32.5385 | 0.8639 | 7.4721 | 7.3672 | 7.2788 | 127 | 7 | 22 | 5
128 | 2026-02-14 16:55 | 29.0766 | 1991.1076 | Phase2_Stabilization | 91.3267 | 7.9663 | 64.6458 | 52.916 | 56.3883 | 48.9202 | 137.5479 | 25.1927 | 28.8815 | 414.0692 | 45.6004 | 8.3297 | 32.5364 | 0.86609 | 6.8925 | 7.514 | 8.1446 | 127 | 7 | 22 | 5
129 | 2026-02-14 16:55 | 29.3038 | 1912.3274 | Phase2_Stabilization | 91.1292 | 7.9452 | 64.6519 | 52.8542 | 56.5281 | 48.5737 | 134.592 | 25.5124 | 28.3803 | 416.5814 | 45.8086 | 8.3533 | 32.5257 | 0.87045 | 7.4369 | 7.3581 | 7.2697 | 127 | 7 | 22 | 5
130 | 2026-02-14 16:56 | 29.5309 | 1764.1809 | Phase2_Stabilization | 91.3238 | 7.9776 | 64.1921 | 53.0708 | 56.4787 | 48.4669 | 134.2594 | 25.3772 | 28.5156 | 415.8725 | 45.6975 | 8.4114 | 32.4495 | 0.88019 | 7.7299 | 7.673 | 4.6812 | 127 | 7 | 22 | 5
131 | 2026-02-14 16:56 | 29.7581 | 2032.553 | Phase2_Stabilization | 91.5097 | 7.912 | 64.2458 | 53.3425 | 56.0827 | 48.4046 | 135.3558 | 25.4822 | 28.3034 | 415.1169 | 45.5759 | 8.3365 | 32.5432 | 0.87247 | 6.2372 | 7.4275 | 6.4258 | 127 | 7 | 22 | 5
132 | 2026-02-14 16:56 | 29.9853 | 1871.335 | Phase2_Stabilization | 92.1556 | 7.9375 | 64.7854 | 52.945 | 56.4158 | 48.3784 | 135.7426 | 25.3862 | 28.5653 | 416.3586 | 45.9735 | 8.2905 | 32.552 | 0.86394 | 7.3955 | 7.4844 | 8.0072 | 127 | 7 | 22 | 5
133 | 2026-02-14 16:56 | 30.2124 | 2126.6902 | Phase2_Stabilization | 92.3196 | 7.9516 | 64.6298 | 52.6485 | 56.3408 | 48.7325 | 136.2833 | 25.0628 | 28.6103 | 414.4582 | 45.6373 | 8.3154 | 32.5623 | 0.87837 | 6.6692 | 7.1453 | 11.5866 | 127 | 7 | 22 | 5
134 | 2026-02-14 16:56 | 30.4396 | 1924.522 | Phase2_Stabilization | 91.3837 | 8.0078 | 64.8606 | 53.0717 | 55.8739 | 48.823 | 135.2907 | 25.3273 | 28.6393 | 416.2199 | 45.7041 | 8.3578 | 32.4434 | 0.86998 | 8.2897 | 7.2056 | 13.5183 | 127 | 7 | 22 | 5
135 | 2026-02-14 16:57 | 30.6667 | 2325.6926 | Phase2_Stabilization | 90.928 | 7.9575 | 64.7816 | 53.1921 | 56.0965 | 48.8884 | 135.5306 | 25.4851 | 28.4275 | 415.3835 | 46.0606 | 8.3194 | 32.4812 | 0.87206 | 6.393 | 7.5024 | 11.7593 | 127 | 7 | 22 | 5
136 | 2026-02-14 16:57 | 30.8939 | 1976.661 | Phase2_Stabilization | 91.91 | 7.9241 | 64.1222 | 53.5306 | 56.5125 | 48.7265 | 136.1899 | 25.2799 | 28.2936 | 416.2189 | 45.8295 | 8.3094 | 32.5746 | 0.87151 | 7.6689 | 7.2322 | 6.336 | 127 | 7 | 22 | 5
137 | 2026-02-14 16:57 | 31.1211 | 2064.1373 | Phase2_Stabilization | 91.4067 | 7.9003 | 64.8085 | 53.2159 | 56.5849 | 48.7052 | 136.3227 | 25.2748 | 28.624 | 414.429 | 45.7791 | 8.381 | 32.3798 | 0.86956 | 7.2119 | 7.9633 | 6.2066 | 127 | 7 | 22 | 5
138 | 2026-02-14 16:57 | 31.3482 | 2256.9592 | Phase2_Stabilization | 91.8869 | 7.9968 | 64.2264 | 53.1755 | 56.3053 | 48.5289 | 134.0567 | 25.3221 | 28.7082 | 415.8848 | 45.6609 | 8.2253 | 32.4133 | 0.87655 | 7.0498 | 7.0817 | 7.933 | 127 | 7 | 22 | 5
139 | 2026-02-14 16:58 | 31.5754 | 1953.0417 | Phase2_Stabilization | 91.7886 | 8.0372 | 64.5436 | 53.4462 | 56.1093 | 48.4411 | 135.4446 | 24.9753 | 28.4069 | 416.4296 | 45.8317 | 8.3468 | 32.5932 | 0.86798 | 6.451 | 7.3286 | 13.0664 | 127 | 7 | 22 | 5
140 | 2026-02-14 16:58 | 31.8025 | 2196.2794 | Phase2_Stabilization | 90.8225 | 7.9598 | 64.7452 | 52.6393 | 56.3199 | 48.6794 | 136.2485 | 25.5544 | 28.564 | 414.6193 | 46.0241 | 8.3347 | 32.4801 | 0.86274 | 7.0421 | 7.4852 | 8.2286 | 127 | 7 | 22 | 5
141 | 2026-02-14 16:58 | 32.0297 | 2380.3698 | Phase2_Stabilization | 92.2902 | 8.0102 | 64.7298 | 53.0616 | 55.7638 | 48.6932 | 135.0288 | 25.2405 | 28.2381 | 416.8614 | 45.7876 | 8.3196 | 32.6177 | 0.88024 | 5.5097 | 7.4059 | 5.2822 | 127 | 7 | 22 | 5
142 | 2026-02-14 16:59 | 32.2569 | 1940.5121 | Phase2_Stabilization | 92.3449 | 7.9599 | 65.5563 | 53.4636 | 56.4219 | 48.732 | 137.5661 | 25.4715 | 28.6195 | 414.5804 | 45.7452 | 8.2885 | 32.5179 | 0.88023 | 7.3288 | 7.2677 | 7.245 | 127 | 7 | 22 | 5
143 | 2026-02-14 16:59 | 32.484 | 2235.8913 | Phase2_Stabilization | 91.4438 | 8.0194 | 64.7337 | 53.1475 | 56.796 | 48.6132 | 135.191 | 25.303 | 28.5044 | 417.4425 | 45.4182 | 8.2698 | 32.5731 | 0.86759 | 7.097 | 7.319 | 10.2106 | 127 | 7 | 22 | 5
144 | 2026-02-14 16:59 | 32.7112 | 2263.0798 | Phase2_Stabilization | 91.6884 | 7.9301 | 64.3831 | 52.9327 | 55.9777 | 48.5582 | 135.8782 | 25.5019 | 28.499 | 417.3642 | 45.7377 | 8.2612 | 32.5429 | 0.86013 | 7.1057 | 7.3136 | 10.037 | 127 | 7 | 22 | 5
145 | 2026-02-14 16:59 | 32.9383 | 2360.0456 | Phase2_Stabilization | 91.6624 | 7.9845 | 64.7245 | 53.157 | 56.0884 | 48.9896 | 136.2192 | 25.4708 | 28.5642 | 415.0421 | 45.7824 | 8.3084 | 32.501 | 0.87562 | 4.9392 | 7.4841 | 7.4481 | 127 | 7 | 22 | 5
146 | 2026-02-14 17:00 | 33.1655 | 2060.1283 | Phase2_Stabilization | 91.8691 | 7.9691 | 64.5376 | 52.4053 | 56.4429 | 48.7758 | 135.4856 | 25.4146 | 28.5187 | 416.939 | 45.9701 | 8.4044 | 32.489 | 0.88416 | 6.2386 | 7.9071 | 10.1725 | 127 | 7 | 22 | 5
147 | 2026-02-14 17:00 | 33.3927 | 2062.5179 | Phase2_Stabilization | 91.8082 | 7.9332 | 64.4209 | 53.0224 | 56.6143 | 48.5586 | 134.1475 | 25.1574 | 28.6217 | 415.8012 | 45.6996 | 8.3589 | 32.5204 | 0.87553 | 6.3496 | 7.5398 | 2.4119 | 127 | 7 | 22 | 5
148 | 2026-02-14 17:00 | 33.6198 | 2365.7515 | Phase2_Stabilization | 92.6311 | 7.9456 | 65.1055 | 53.22 | 56.064 | 48.6914 | 135.1617 | 25.4655 | 28.4164 | 415.6724 | 46.113 | 8.3482 | 32.4985 | 0.86778 | 6.9 | 7.7805 | 8.3302 | 127 | 7 | 22 | 5
149 | 2026-02-14 17:00 | 33.847 | 2346.0451 | Phase2_Stabilization | 91.4973 | 7.8315 | 64.4976 | 52.8626 | 56.2988 | 48.7656 | 136.703 | 25.0764 | 28.4822 | 416.1492 | 45.7281 | 8.2962 | 32.5153 | 0.8749 | 7.1533 | 7.6107 | 10.6703 | 127 | 7 | 22 | 5
150 | 2026-02-14 17:01 | 34.0741 | 2354.2165 | Phase2_Stabilization | 91.0854 | 7.9202 | 64.3223 | 53.2714 | 56.0133 | 48.4637 | 135.3615 | 25.3979 | 28.4724 | 414.0614 | 45.9322 | 8.3386 | 32.5943 | 0.88219 | 6.693 | 7.7321 | 6.3904 | 127 | 7 | 22 | 5
151 | 2026-02-14 17:01 | 34.3013 | 2384.6396 | Phase2_Stabilization | 90.9504 | 7.9342 | 64.6669 | 53.1233 | 56.3841 | 48.6841 | 134.9587 | 25.2518 | 28.376 | 415.6499 | 45.6079 | 8.3407 | 32.4302 | 0.87318 | 7.2403 | 6.9398 | 6.2676 | 127 | 7 | 22 | 5
152 | 2026-02-14 17:01 | 34.5285 | 2239.7289 | Phase2_Stabilization | 91.4553 | 7.847 | 64.559 | 53.0745 | 56.8 | 48.2531 | 136.6842 | 25.5212 | 28.8046 | 415.515 | 45.9141 | 8.3352 | 32.4283 | 0.86336 | 6.3419 | 7.4517 | 3.6438 | 127 | 7 | 22 | 5
153 | 2026-02-14 17:01 | 34.7556 | 2397.6691 | Phase2_Stabilization | 91.7609 | 7.8855 | 64.8766 | 53.0537 | 56.4099 | 48.8486 | 135.2595 | 25.4674 | 28.4489 | 415.924 | 45.5458 | 8.2258 | 32.4385 | 0.87371 | 7.1225 | 7.801 | 12.265 | 127 | 7 | 22 | 5
154 | 2026-02-14 17:02 | 34.9828 | 2422.6035 | Phase2_Stabilization | 92.5576 | 7.9638 | 64.4143 | 52.8991 | 56.3297 | 48.3387 | 135.0861 | 25.4149 | 28.4762 | 413.9636 | 46.0015 | 8.2957 | 32.6136 | 0.88147 | 7.0143 | 7.4185 | 6.3361 | 127 | 7 | 22 | 5
155 | 2026-02-14 17:02 | 35.21 | 2280.6684 | Phase2_Stabilization | 91.6517 | 8.0611 | 64.5622 | 53.1595 | 56.4388 | 48.57 | 135.7918 | 25.3909 | 28.4005 | 415.675 | 45.4704 | 8.3503 | 32.5909 | 0.87911 | 7.0722 | 7.8799 | 9.0229 | 127 | 7 | 22 | 5
156 | 2026-02-14 17:02 | 35.4371 | 2699.142 | Phase2_Stabilization | 91.864 | 7.9421 | 64.1862 | 53.0698 | 56.2263 | 48.5157 | 136.6745 | 25.1804 | 28.7997 | 416.6391 | 45.6558 | 8.3633 | 32.5413 | 0.8694 | 6.9912 | 7.813 | 10.0882 | 127 | 7 | 22 | 5
157 | 2026-02-14 17:02 | 35.6643 | 2497.1417 | Phase2_Stabilization | 91.9824 | 7.9024 | 64.6827 | 53.3212 | 56.1475 | 48.5847 | 137.5996 | 25.2957 | 28.6165 | 414.9569 | 45.9155 | 8.3338 | 32.5087 | 0.87712 | 7.9842 | 7.4308 | 12.1973 | 127 | 7 | 22 | 5
158 | 2026-02-14 17:03 | 35.8914 | 2252.4658 | Phase2_Stabilization | 92.1489 | 7.9641 | 64.766 | 52.9223 | 56.491 | 48.7302 | 136.9504 | 25.4184 | 28.4316 | 415.8172 | 45.596 | 8.3598 | 32.6012 | 0.87553 | 7.6157 | 7.3914 | 8.354 | 127 | 7 | 22 | 5
159 | 2026-02-14 17:03 | 36.1186 | 2556.5522 | Phase2_Stabilization | 93.5 | 7.9821 | 64.5252 | 53.2274 | 56.4614 | 48.3706 | 136.7512 | 25.4216 | 28.6368 | 415.9412 | 45.518 | 8.341 | 32.3751 | 0.87244 | 6.2788 | 7.2973 | 7.2499 | 127 | 7 | 22 | 5
160 | 2026-02-14 17:03 | 36.3458 | 2317.172 | Phase2_Stabilization | 91.435 | 7.9331 | 64.9697 | 53.4192 | 56.3749 | 48.6743 | 135.1241 | 25.4433 | 28.542 | 415.3981 | 45.9755 | 8.3339 | 32.5335 | 0.8628 | 6.8924 | 7.3958 | 8.8406 | 127 | 7 | 22 | 5
161 | 2026-02-14 17:03 | 36.5729 | 2607.8102 | Phase2_Stabilization | 91.31 | 7.9378 | 64.7874 | 52.8166 | 56.1188 | 48.5796 | 134.7455 | 25.3787 | 28.597 | 415.8114 | 45.751 | 8.2564 | 32.5443 | 0.87428 | 7.2677 | 7.2822 | 11.5726 | 127 | 7 | 22 | 5
162 | 2026-02-14 17:04 | 36.8001 | 2681.2776 | Phase2_Stabilization | 92.1306 | 7.9484 | 64.591 | 53.2127 | 56.6113 | 48.6765 | 135.8109 | 25.2452 | 28.601 | 416.1867 | 45.5853 | 8.3191 | 32.6195 | 0.87827 | 6.5102 | 7.6363 | 7.6978 | 127 | 7 | 22 | 5
163 | 2026-02-14 17:04 | 37.0272 | 2387.5299 | Phase2_Stabilization | 92.2465 | 7.9012 | 64.2478 | 53.2936 | 56.6397 | 48.5472 | 135.887 | 25.2984 | 28.4705 | 414.0519 | 45.738 | 8.3182 | 32.5238 | 0.86732 | 7.6437 | 7.2281 | 5.9767 | 127 | 7 | 22 | 5
164 | 2026-02-14 17:04 | 37.2544 | 2681.6503 | Phase2_Stabilization | 92.8522 | 7.946 | 64.3587 | 53.3632 | 56.2599 | 48.776 | 134.8524 | 25.3499 | 28.6404 | 416.1499 | 46.2107 | 8.2927 | 32.5214 | 0.87576 | 7.1426 | 7.6608 | 4.3631 | 127 | 7 | 22 | 5
165 | 2026-02-14 17:04 | 37.4816 | 2611.0761 | Phase2_Stabilization | 92.1844 | 8.0253 | 64.7646 | 53.5227 | 56.5548 | 48.4754 | 135.2784 | 25.1061 | 28.5959 | 415.6334 | 45.906 | 8.3516 | 32.4885 | 0.86558 | 5.0934 | 7.703 | 4.7304 | 127 | 7 | 22 | 5
166 | 2026-02-14 17:04 | 37.7087 | 2690.4433 | Phase2_Stabilization | 91.666 | 7.9483 | 64.6072 | 52.7661 | 55.9941 | 48.3711 | 136.4366 | 25.632 | 28.8166 | 415.6578 | 45.9526 | 8.2811 | 32.4667 | 0.86512 | 7.3651 | 7.1739 | 10.8235 | 127 | 7 | 22 | 5
167 | 2026-02-14 17:05 | 37.9359 | 2873.7605 | Phase2_Stabilization | 91.9028 | 7.9356 | 64.5663 | 52.9393 | 56.2182 | 48.6709 | 136.0546 | 25.3628 | 28.3821 | 415.3004 | 45.8753 | 8.3328 | 32.5463 | 0.86779 | 6.626 | 7.8439 | 7.6625 | 127 | 7 | 22 | 5
168 | 2026-02-14 17:05 | 38.163 | 2554.5658 | Phase2_Stabilization | 92.3229 | 7.9509 | 64.4437 | 52.9916 | 56.0556 | 48.7352 | 136.1344 | 25.5157 | 28.6583 | 415.2082 | 45.7966 | 8.3358 | 32.4738 | 0.87752 | 7.2139 | 7.6107 | 7.2017 | 127 | 7 | 22 | 5
169 | 2026-02-14 17:05 | 38.3902 | 2490.591 | Phase2_Stabilization | 91.8503 | 7.9174 | 64.0312 | 53.0209 | 56.0025 | 48.9128 | 136.4482 | 25.1835 | 28.5319 | 416.1918 | 45.2994 | 8.4029 | 32.5759 | 0.86961 | 7.8693 | 7.656 | 6.9774 | 127 | 7 | 22 | 5
170 | 2026-02-14 17:06 | 38.6174 | 2484.8151 | Phase2_Stabilization | 91.9048 | 7.9671 | 64.3144 | 53.5359 | 56.5191 | 48.4976 | 135.5053 | 25.4014 | 28.6706 | 416.0481 | 45.7305 | 8.3089 | 32.5482 | 0.86739 | 7.1587 | 7.3846 | 8.5675 | 127 | 7 | 22 | 5
171 | 2026-02-14 17:06 | 38.8445 | 2511.7623 | Phase2_Stabilization | 92.4293 | 7.9653 | 64.7682 | 52.9138 | 55.6667 | 48.8575 | 135.2319 | 25.5639 | 28.6196 | 415.3793 | 45.8325 | 8.3052 | 32.4965 | 0.87773 | 7.914 | 7.6516 | 7.9535 | 127 | 7 | 22 | 5
172 | 2026-02-14 17:06 | 39.0717 | 2642.5893 | Phase2_Stabilization | 92.1022 | 7.9455 | 64.5201 | 53.1509 | 56.1256 | 48.2826 | 134.9984 | 25.1914 | 28.464 | 414.2223 | 45.5327 | 8.333 | 32.5854 | 0.87017 | 6.9686 | 7.7462 | 7.9905 | 127 | 7 | 22 | 5
173 | 2026-02-14 17:06 | 39.2989 | 2723.3584 | Phase2_Stabilization | 92.8524 | 8.0055 | 64.7145 | 53.2671 | 56.085 | 48.3194 | 137.485 | 25.4445 | 28.6689 | 415.7457 | 45.5005 | 8.2788 | 32.3909 | 0.86345 | 7.4937 | 7.4984 | 12.1127 | 127 | 7 | 22 | 5
174 | 2026-02-14 17:06 | 39.526 | 2728.7228 | Phase2_Stabilization | 92.3062 | 7.9795 | 64.4083 | 52.9103 | 56.2989 | 48.5223 | 135.8216 | 25.3045 | 28.2247 | 415.9349 | 45.3785 | 8.2988 | 32.4692 | 0.86588 | 7.4669 | 7.9456 | 12.4035 | 127 | 7 | 22 | 5
175 | 2026-02-14 17:07 | 39.7532 | 2830.1488 | Phase2_Stabilization | 91.521 | 7.9035 | 64.4554 | 53.0056 | 56.4726 | 48.2764 | 135.623 | 25.1676 | 28.4151 | 417.2096 | 45.7923 | 8.3225 | 32.5368 | 0.8659 | 6.8736 | 7.5267 | 4.5831 | 127 | 7 | 22 | 5
176 | 2026-02-14 17:07 | 39.9803 | 2718.4 | Phase2_Stabilization | 91.9658 | 8.031 | 64.4453 | 52.9007 | 56.1361 | 48.3821 | 135.1988 | 25.4292 | 28.4896 | 414.9765 | 45.9499 | 8.3419 | 32.4949 | 0.86929 | 7.5783 | 7.7696 | 9.3285 | 127 | 7 | 22 | 5
177 | 2026-02-14 17:07 | 40.2075 | 2958.8584 | Phase2_Stabilization | 92.4928 | 7.9943 | 64.8395 | 52.9939 | 56.0148 | 48.6728 | 138.1294 | 25.4689 | 28.435 | 415.7675 | 45.9097 | 8.2909 | 32.6261 | 0.87513 | 6.4423 | 7.6096 | 6.3455 | 127 | 7 | 22 | 5
178 | 2026-02-14 17:07 | 40.4347 | 2705.895 | Phase2_Stabilization | 91.3352 | 7.9471 | 64.6126 | 53.2059 | 56.1344 | 48.5328 | 135.192 | 25.3106 | 28.4835 | 415.443 | 45.9039 | 8.3518 | 32.5047 | 0.88316 | 6.8783 | 7.625 | 8.2677 | 127 | 7 | 22 | 5
179 | 2026-02-14 17:08 | 40.6618 | 3187.5864 | Phase2_Stabilization | 92.0626 | 7.9357 | 64.5407 | 52.7218 | 56.354 | 48.6182 | 135.578 | 25.5013 | 28.4624 | 413.5768 | 45.626 | 8.2682 | 32.527 | 0.87464 | 6.1731 | 7.1453 | 9.92 | 127 | 7 | 22 | 5
180 | 2026-02-14 17:08 | 40.889 | 2875.8397 | Phase2_Stabilization | 91.5375 | 8.0234 | 64.3329 | 52.7919 | 56.3751 | 48.6865 | 136.0583 | 25.2279 | 28.6925 | 415.1961 | 45.3565 | 8.3302 | 32.5521 | 0.87296 | 7.0184 | 7.6261 | 7.8238 | 127 | 7 | 22 | 5
181 | 2026-02-14 17:08 | 41.1161 | 2659.6426 | Phase2_Stabilization | 91.7946 | 7.9787 | 63.983 | 53.0662 | 56.5242 | 48.5705 | 136.5096 | 25.1385 | 28.6071 | 415.934 | 45.3442 | 8.3174 | 32.4711 | 0.86777 | 7.3073 | 7.3771 | 9.2496 | 127 | 7 | 22 | 5
182 | 2026-02-14 17:08 | 41.3433 | 2641.6891 | Phase2_Stabilization | 92.5295 | 8.017 | 64.7889 | 53.4442 | 56.0749 | 48.7791 | 136.758 | 25.4283 | 28.483 | 414.8441 | 45.5723 | 8.325 | 32.6021 | 0.87002 | 7.8286 | 7.3561 | 10.3726 | 127 | 7 | 22 | 5
183 | 2026-02-14 17:09 | 41.5705 | 2899.7731 | Phase2_Stabilization | 91.954 | 8.0169 | 64.408 | 53.1434 | 56.4181 | 48.6627 | 137.5319 | 25.4095 | 28.517 | 416.85 | 45.5852 | 8.2946 | 32.4406 | 0.87211 | 7.6243 | 7.858 | 9.7838 | 127 | 7 | 22 | 5
184 | 2026-02-14 17:09 | 41.7976 | 2804.9333 | Phase2_Stabilization | 91.8572 | 7.9615 | 64.3821 | 53.1881 | 56.7354 | 48.4446 | 135.6545 | 25.2981 | 28.5396 | 415.9941 | 45.9237 | 8.3347 | 32.5147 | 0.8788 | 6.2948 | 7.5149 | 6.6628 | 127 | 7 | 22 | 5
185 | 2026-02-14 17:09 | 42.0248 | 2966.8077 | Phase2_Stabilization | 91.1287 | 7.9939 | 64.4431 | 53.0435 | 56.5449 | 48.6868 | 135.1584 | 25.5133 | 28.6757 | 415.0315 | 45.5416 | 8.2579 | 32.5442 | 0.87511 | 6.3433 | 7.317 | 7.171 | 127 | 7 | 22 | 5
186 | 2026-02-14 17:10 | 42.2519 | 2944.6323 | Phase2_Stabilization | 92.3183 | 7.9105 | 64.375 | 52.8447 | 56.3515 | 48.5842 | 135.8808 | 25.4006 | 28.683 | 416.6379 | 45.8071 | 8.4332 | 32.5353 | 0.88319 | 7.4462 | 7.454 | 5.0509 | 127 | 7 | 22 | 5
187 | 2026-02-14 17:10 | 42.4791 | 2874.7655 | Phase2_Stabilization | 92.2393 | 7.9797 | 64.7766 | 53.4537 | 56.379 | 48.301 | 136.1058 | 25.5014 | 28.5672 | 415.3194 | 45.9821 | 8.3488 | 32.46 | 0.86858 | 7.6977 | 7.2703 | 6.4474 | 127 | 7 | 22 | 5
188 | 2026-02-14 17:10 | 42.7063 | 2769.2989 | Phase2_Stabilization | 92.7326 | 7.8914 | 64.5766 | 53.2538 | 56.2299 | 48.6463 | 138.0348 | 25.3874 | 28.5041 | 416.4704 | 45.7039 | 8.3285 | 32.5637 | 0.86886 | 7.8257 | 7.8215 | 13.7816 | 127 | 7 | 22 | 5
189 | 2026-02-14 17:10 | 42.9334 | 2680.3767 | Phase2_Stabilization | 91.511 | 7.9031 | 64.7215 | 53.5561 | 56.4123 | 48.5626 | 134.3878 | 25.3774 | 28.4223 | 416.0226 | 46.0794 | 8.3422 | 32.4573 | 0.85935 | 7.449 | 7.3971 | 6.599 | 127 | 7 | 22 | 5
190 | 2026-02-14 17:10 | 43.1606 | 2862.694 | Phase2_Stabilization | 92.1187 | 7.9766 | 64.0015 | 52.9321 | 56.1297 | 48.514 | 136.453 | 25.2963 | 28.4311 | 415.8913 | 45.606 | 8.353 | 32.5785 | 0.8725 | 6.5137 | 7.6535 | 5.5214 | 127 | 7 | 22 | 5
191 | 2026-02-14 17:11 | 43.3878 | 3081.6552 | Phase2_Stabilization | 92.1489 | 7.9903 | 64.756 | 53.6294 | 56.3182 | 48.6869 | 135.7975 | 25.5502 | 28.5255 | 415.1932 | 45.8469 | 8.2832 | 32.5695 | 0.87633 | 6.502 | 7.8293 | 9.3275 | 127 | 7 | 22 | 5
192 | 2026-02-14 17:11 | 43.6149 | 2996.7551 | Phase2_Stabilization | 92.6895 | 7.9438 | 64.5026 | 53.2753 | 56.4492 | 48.727 | 136.46 | 25.266 | 28.6713 | 415.6289 | 45.709 | 8.3544 | 32.4948 | 0.87232 | 6.4132 | 7.4613 | 8.0849 | 127 | 7 | 22 | 5
193 | 2026-02-14 17:11 | 43.8421 | 2784.1496 | Phase2_Stabilization | 91.6944 | 7.9171 | 64.5985 | 53.3146 | 56.0431 | 48.5129 | 135.9485 | 25.5705 | 28.5923 | 415.8639 | 45.7515 | 8.3037 | 32.4227 | 0.87456 | 7.0767 | 7.6227 | 8.507 | 127 | 7 | 22 | 5
194 | 2026-02-14 17:11 | 44.0692 | 3021.2319 | Phase2_Stabilization | 92.0537 | 7.9016 | 64.377 | 53.1992 | 56.0688 | 48.4214 | 135.4561 | 25.3455 | 28.4854 | 415.6343 | 46.0801 | 8.3827 | 32.4791 | 0.87285 | 7.1606 | 7.2945 | 12.7257 | 127 | 7 | 22 | 5
195 | 2026-02-14 17:12 | 44.2964 | 3069.8035 | Phase2_Stabilization | 92.2043 | 7.9473 | 63.9734 | 53.02 | 56.1818 | 48.823 | 136.3125 | 25.1722 | 28.6662 | 416.3582 | 46.0244 | 8.3014 | 32.5905 | 0.86682 | 6.9749 | 8.0785 | 9.6492 | 127 | 7 | 22 | 5
196 | 2026-02-14 17:12 | 44.5236 | 2886.9805 | Phase2_Stabilization | 91.6505 | 7.9743 | 64.7068 | 53.3951 | 55.9176 | 48.6751 | 136.7945 | 25.5562 | 28.5504 | 416.9489 | 45.6344 | 8.2129 | 32.5988 | 0.86933 | 7.1969 | 7.7043 | 7.711 | 127 | 7 | 22 | 5
197 | 2026-02-14 17:12 | 44.7507 | 3064.4945 | Phase2_Stabilization | 91.5635 | 7.8563 | 64.2676 | 53.1886 | 56.0821 | 48.9584 | 136.5454 | 25.4068 | 28.5104 | 415.567 | 45.8432 | 8.399 | 32.493 | 0.87327 | 6.7889 | 7.5136 | 7.487 | 127 | 7 | 22 | 5
198 | 2026-02-14 17:12 | 44.9779 | 3065.0079 | Phase2_Stabilization | 91.6763 | 7.9874 | 63.9532 | 52.7326 | 56.3775 | 48.6967 | 136.0765 | 25.5082 | 28.5267 | 414.724 | 45.8215 | 8.3823 | 32.4017 | 0.87163 | 6.645 | 7.394 | 7.3093 | 127 | 7 | 22 | 5
199 | 2026-02-14 17:13 | 45.205 | 2892.8064 | Phase2_Stabilization | 92.2754 | 8.0469 | 64.0687 | 52.9553 | 56.1895 | 48.8273 | 135.6978 | 25.5421 | 28.288 | 416.3485 | 45.7693 | 8.2811 | 32.4739 | 0.87232 | 7.8624 | 7.4897 | 11.3375 | 127 | 7 | 22 | 5
200 | 2026-02-14 17:13 | 45.4322 | 3142.6727 | Phase2_Stabilization | 91.2569 | 7.9346 | 64.5558 | 53.0028 | 56.3833 | 48.514 | 134.4294 | 25.3704 | 28.4878 | 415.3623 | 46.0009 | 8.2961 | 32.3455 | 0.86373 | 6.9245 | 7.4855 | 7.7999 | 127 | 7 | 22 | 5
201 | 2026-02-14 17:13 | 45.6594 | 3189.8166 | Phase2_Stabilization | 92.1138 | 7.9924 | 64.3987 | 53.2147 | 56.3913 | 48.938 | 136.3442 | 25.2816 | 28.6622 | 416.8155 | 45.8583 | 8.2708 | 32.5964 | 0.86593 | 6.7044 | 7.9659 | 3.8884 | 127 | 7 | 22 | 5
202 | 2026-02-14 17:13 | 45.8865 | 3286.8334 | Phase2_Stabilization | 91.1047 | 7.8882 | 64.9671 | 53.197 | 55.7876 | 48.603 | 136.0533 | 25.4849 | 28.473 | 415.2282 | 46.1944 | 8.3 | 32.5206 | 0.8621 | 6.3585 | 7.3033 | 8.5007 | 127 | 7 | 22 | 5
203 | 2026-02-14 17:14 | 46.1137 | 3297.6984 | Phase2_Stabilization | 92.3554 | 7.9795 | 64.2597 | 53.2284 | 56.3176 | 48.4731 | 134.997 | 25.3845 | 28.5249 | 415.0157 | 45.5462 | 8.2508 | 32.4952 | 0.87301 | 6.0561 | 7.5749 | 4.7998 | 127 | 7 | 22 | 5
204 | 2026-02-14 17:14 | 46.3408 | 2933.3138 | Phase2_Stabilization | 91.0972 | 7.9095 | 63.88 | 52.729 | 56.7489 | 48.689 | 135.262 | 25.4339 | 28.5981 | 416.2235 | 45.6973 | 8.351 | 32.4289 | 0.86644 | 7.7194 | 7.5441 | 14.3236 | 127 | 7 | 22 | 5
205 | 2026-02-14 17:14 | 46.568 | 3017.4555 | Phase2_Stabilization | 91.5975 | 8.0129 | 64.1799 | 53.2125 | 56.3102 | 48.8705 | 135.5099 | 25.1067 | 28.62 | 414.4611 | 45.7517 | 8.3153 | 32.3989 | 0.87178 | 7.372 | 7.518 | 6.3535 | 127 | 7 | 22 | 5
206 | 2026-02-14 17:14 | 46.7952 | 3259.8397 | Phase2_Stabilization | 92.1131 | 7.9931 | 64.7229 | 52.9489 | 56.2807 | 48.6473 | 134.3149 | 25.4197 | 28.4907 | 415.3615 | 45.8531 | 8.2257 | 32.4419 | 0.88352 | 5.6676 | 7.5603 | 7.9187 | 127 | 7 | 22 | 5
207 | 2026-02-14 17:15 | 47.0223 | 3275.0785 | Phase2_Stabilization | 92.456 | 7.9945 | 64.3103 | 53.2293 | 56.1391 | 48.3164 | 135.6347 | 25.3331 | 28.584 | 416.0554 | 45.6306 | 8.2462 | 32.5461 | 0.874 | 7.8387 | 7.4711 | 10.1003 | 127 | 7 | 22 | 5
208 | 2026-02-14 17:15 | 47.2495 | 3290.7095 | Phase2_Stabilization | 91.7375 | 7.9904 | 64.339 | 53.0469 | 56.2851 | 48.7527 | 134.6871 | 25.5235 | 28.7445 | 414.1565 | 45.9533 | 8.3324 | 32.4615 | 0.87737 | 7.4042 | 7.7493 | 7.7755 | 127 | 7 | 22 | 5
209 | 2026-02-14 17:15 | 47.4766 | 3827.5206 | Phase2_Stabilization | 91.4342 | 8.0161 | 64.6469 | 53.3553 | 56.0651 | 48.4937 | 135.3801 | 25.4977 | 28.427 | 415.759 | 45.8108 | 8.305 | 32.44 | 0.87186 | 6.9514 | 7.6848 | 7.9151 | 127 | 7 | 22 | 5
210 | 2026-02-14 17:16 | 47.7038 | 3330.3005 | Phase2_Stabilization | 92.9686 | 7.9631 | 64.5548 | 52.8445 | 55.9713 | 48.5987 | 135.2602 | 25.3857 | 28.4713 | 415.1427 | 45.7413 | 8.2974 | 32.5751 | 0.88046 | 8.04 | 7.6392 | 9.8331 | 127 | 7 | 22 | 5
211 | 2026-02-14 17:16 | 47.931 | 3433.9419 | Phase2_Stabilization | 91.0204 | 7.9457 | 64.6694 | 53.4205 | 56.217 | 48.6102 | 134.5598 | 25.4367 | 28.7344 | 415.5872 | 45.5403 | 8.3181 | 32.4921 | 0.86878 | 7.1648 | 6.9296 | 12.6932 | 127 | 7 | 22 | 5
212 | 2026-02-14 17:16 | 48.1581 | 3421.0139 | Phase2_Stabilization | 90.6541 | 7.9677 | 64.7664 | 53.3278 | 56.4606 | 48.6125 | 137.7448 | 25.2434 | 28.5555 | 416.1795 | 45.6525 | 8.3383 | 32.529 | 0.86975 | 6.1997 | 7.6051 | 10.8666 | 127 | 7 | 22 | 5
213 | 2026-02-14 17:16 | 48.3853 | 3389.1772 | Phase2_Stabilization | 92.0549 | 7.9526 | 64.5272 | 53.4194 | 56.157 | 48.7549 | 136.5861 | 25.5778 | 28.3207 | 416.0343 | 45.9557 | 8.4058 | 32.5584 | 0.87596 | 6.965 | 7.2424 | 12.2214 | 127 | 7 | 22 | 5
214 | 2026-02-14 17:17 | 48.6125 | 3253.6098 | Phase2_Stabilization | 91.3411 | 8 | 63.9946 | 53.1913 | 55.9515 | 48.3712 | 135.4725 | 25.6448 | 28.2862 | 415.8042 | 45.7616 | 8.3588 | 32.4846 | 0.87642 | 7.3448 | 7.6462 | 6.6284 | 127 | 7 | 22 | 5
215 | 2026-02-14 17:17 | 48.8396 | 3436.8497 | Phase2_Stabilization | 91.3463 | 8.035 | 64.2371 | 53.2497 | 56.2747 | 48.8974 | 136.1461 | 25.4763 | 28.5867 | 415.2732 | 46.003 | 8.255 | 32.4349 | 0.87354 | 6.626 | 7.8669 | 9.4964 | 127 | 7 | 22 | 5
216 | 2026-02-14 17:17 | 49.0668 | 3213.0031 | Phase2_Stabilization | 92.0049 | 7.865 | 64.6255 | 53.1062 | 56.529 | 48.4565 | 136.557 | 25.5388 | 28.4639 | 416.6429 | 45.967 | 8.3378 | 32.6402 | 0.87976 | 7.6275 | 7.3585 | 9.2979 | 127 | 7 | 22 | 5
217 | 2026-02-14 17:17 | 49.2939 | 3312.1662 | Phase2_Stabilization | 91.9576 | 8.0275 | 64.2366 | 53.2474 | 56.0527 | 48.4348 | 136.6606 | 25.3135 | 28.5282 | 415.772 | 45.9345 | 8.2803 | 32.5636 | 0.87186 | 5.728 | 7.5163 | 9.5439 | 127 | 7 | 22 | 5
218 | 2026-02-14 17:18 | 49.5211 | 3288.7751 | Phase2_Stabilization | 91.4026 | 7.9904 | 64.3541 | 53.4802 | 56.4475 | 48.6624 | 135.1561 | 25.3128 | 28.5787 | 414.1058 | 45.6908 | 8.2971 | 32.4437 | 0.87093 | 7.6113 | 7.4362 | 12.3163 | 127 | 7 | 22 | 5
219 | 2026-02-14 17:18 | 49.7483 | 3392.8168 | Phase2_Stabilization | 91.3203 | 8.0046 | 64.6096 | 53.1922 | 56.2056 | 48.6779 | 136.8823 | 25.3843 | 28.8206 | 416.3837 | 45.9279 | 8.3103 | 32.5468 | 0.87939 | 6.4856 | 7.8201 | 8.1483 | 127 | 7 | 22 | 5
220 | 2026-02-14 17:18 | 49.9754 | 3757.0324 | Phase2_Stabilization | 92.2681 | 7.9097 | 64.3763 | 52.984 | 56.6776 | 48.6124 | 136.065 | 25.3633 | 28.6528 | 414.5917 | 45.7893 | 8.2356 | 32.5315 | 0.87116 | 6.8502 | 7.5726 | 7.8619 | 127 | 7 | 22 | 5
221 | 2026-02-14 17:18 | 50.2026 | 3119.211 | Phase2_Stabilization | 92.4389 | 7.9693 | 64.6343 | 53.1945 | 56.1994 | 48.4979 | 134.8492 | 25.3939 | 28.8084 | 416.3271 | 45.7729 | 8.3821 | 32.5561 | 0.87734 | 6.9837 | 7.9328 | 9.9632 | 127 | 7 | 22 | 5
222 | 2026-02-14 17:19 | 50.4297 | 3533.5293 | Phase2_Stabilization | 91.4253 | 7.9809 | 64.1133 | 52.8846 | 56.3998 | 48.7018 | 136.9282 | 25.4325 | 28.8406 | 414.9061 | 45.6308 | 8.3111 | 32.4689 | 0.87275 | 7.626 | 7.6405 | 4.3469 | 127 | 7 | 22 | 5
223 | 2026-02-14 17:19 | 50.6569 | 3189.8418 | Phase2_Stabilization | 92.9814 | 7.9175 | 64.4901 | 53.1236 | 56.6936 | 48.5995 | 136.957 | 25.4533 | 28.6702 | 415.8473 | 45.9187 | 8.3313 | 32.5316 | 0.86651 | 7.099 | 7.5857 | 8.5496 | 127 | 7 | 22 | 5
224 | 2026-02-14 17:19 | 50.8841 | 3383.4768 | Phase2_Stabilization | 91.3879 | 7.9364 | 64.1897 | 53.3555 | 56.4646 | 48.9393 | 138.3964 | 25.2595 | 28.7128 | 416.4082 | 45.71 | 8.3371 | 32.4992 | 0.87047 | 6.7838 | 7.5813 | 8.4353 | 127 | 7 | 22 | 5
225 | 2026-02-14 17:19 | 51.1112 | 3642.735 | Phase2_Stabilization | 91.0683 | 7.9726 | 64.8621 | 52.6341 | 56.2964 | 48.8632 | 134.8821 | 25.538 | 28.3318 | 415.4578 | 45.7375 | 8.2767 | 32.5022 | 0.88348 | 6.6622 | 7.7322 | 6.4745 | 127 | 7 | 22 | 5
226 | 2026-02-14 17:20 | 51.3384 | 3498.1059 | Phase2_Stabilization | 91.7906 | 8.0053 | 64.7384 | 53.0952 | 56.1745 | 48.6582 | 136.3066 | 25.4603 | 28.6095 | 415.7648 | 45.6149 | 8.3453 | 32.5629 | 0.85934 | 6.1238 | 7.2074 | 11.5557 | 127 | 7 | 22 | 5
227 | 2026-02-14 17:20 | 51.5655 | 3335.1449 | Phase2_Stabilization | 91.5844 | 7.9981 | 64.0286 | 53.0315 | 56.4805 | 48.3002 | 135.4496 | 25.4247 | 28.7371 | 416.0857 | 45.8801 | 8.2772 | 32.4708 | 0.86957 | 6.7748 | 7.5913 | 6.0228 | 127 | 7 | 22 | 5
228 | 2026-02-14 17:20 | 51.7927 | 3407.1955 | Phase2_Stabilization | 91.9823 | 7.9585 | 64.2003 | 53.0856 | 56.1912 | 48.6065 | 136.536 | 25.5752 | 28.6384 | 413.9411 | 45.7128 | 8.2708 | 32.464 | 0.8757 | 7.7 | 7.5678 | 8.3025 | 127 | 7 | 22 | 5
229 | 2026-02-14 17:20 | 52.0199 | 3640.526 | Phase2_Stabilization | 91.8875 | 7.9696 | 64.1014 | 52.8626 | 56.0628 | 48.5268 | 134.4956 | 25.2584 | 28.7197 | 417.1821 | 45.8372 | 8.3812 | 32.5323 | 0.86837 | 6.8664 | 7.6993 | 9.809 | 127 | 7 | 22 | 5
230 | 2026-02-14 17:20 | 52.247 | 3435.7103 | Phase2_Stabilization | 92.1017 | 7.9225 | 64.366 | 53.1267 | 56.2442 | 48.3831 | 134.9311 | 25.369 | 28.7383 | 415.7263 | 46.067 | 8.379 | 32.5066 | 0.87205 | 7.64 | 7.5332 | 12.2703 | 127 | 7 | 22 | 5
231 | 2026-02-14 17:21 | 52.4742 | 3599.0471 | Phase2_Stabilization | 91.1216 | 7.9275 | 64.4112 | 53.3045 | 56.6745 | 48.5827 | 135.1207 | 25.2471 | 28.6314 | 416.3971 | 46.0589 | 8.3481 | 32.5612 | 0.86303 | 7.8606 | 7.3533 | 8.8633 | 127 | 7 | 22 | 5
232 | 2026-02-14 17:21 | 52.7014 | 3587.787 | Phase2_Stabilization | 92.6808 | 7.9595 | 64.0635 | 53.1085 | 56.2925 | 48.4724 | 135.7926 | 25.2148 | 28.7329 | 415.7257 | 45.7654 | 8.3468 | 32.6249 | 0.87913 | 6.4851 | 7.5795 | 11.1531 | 127 | 7 | 22 | 5
233 | 2026-02-14 17:21 | 52.9285 | 3494.3161 | Phase2_Stabilization | 91.7291 | 7.9479 | 64.4111 | 53.1989 | 56.0876 | 48.8268 | 135.4116 | 25.335 | 28.6131 | 416.4519 | 45.491 | 8.3659 | 32.3585 | 0.8666 | 6.9218 | 7.3389 | 10.7786 | 127 | 7 | 22 | 5
234 | 2026-02-14 17:22 | 53.1557 | 3946.44 | Phase2_Stabilization | 92.3658 | 7.9854 | 64.2075 | 53.2581 | 56.2035 | 48.4123 | 136.4031 | 25.2425 | 28.3005 | 415.3908 | 46.3094 | 8.3228 | 32.5639 | 0.87407 | 8.3976 | 7.1867 | 9.0605 | 127 | 7 | 22 | 5
235 | 2026-02-14 17:22 | 53.3828 | 3725.994 | Phase2_Stabilization | 91.9171 | 8.0053 | 64.8315 | 53.3835 | 56.2363 | 49.0685 | 136.6355 | 25.2691 | 28.5257 | 414.8572 | 46.0992 | 8.3142 | 32.4572 | 0.87575 | 7.8616 | 7.726 | 6.0279 | 127 | 7 | 22 | 5
236 | 2026-02-14 17:22 | 53.61 | 3326.0578 | Phase2_Stabilization | 92.2359 | 8.0197 | 64.5066 | 53.1804 | 56.1483 | 48.3997 | 136.3977 | 25.3495 | 28.7051 | 416.4114 | 46.0345 | 8.3246 | 32.576 | 0.87191 | 5.9065 | 7.6787 | 5.3703 | 127 | 7 | 22 | 5
237 | 2026-02-14 17:22 | 53.8372 | 3686.9637 | Phase2_Stabilization | 92.1851 | 7.9484 | 64.1107 | 52.864 | 56.5131 | 48.6924 | 137.1985 | 25.5569 | 28.4347 | 413.7057 | 45.8103 | 8.3767 | 32.4762 | 0.86731 | 7.2203 | 7.6569 | 9.3124 | 127 | 7 | 22 | 5
238 | 2026-02-14 17:23 | 54.0643 | 3569.8945 | Phase2_Stabilization | 92.4541 | 7.8838 | 64.3144 | 53.4139 | 55.9343 | 48.7574 | 136.2183 | 25.4319 | 28.5294 | 416.5108 | 45.8577 | 8.2707 | 32.5492 | 0.87946 | 6.986 | 7.8324 | 7.6159 | 127 | 7 | 22 | 5
239 | 2026-02-14 17:23 | 54.2915 | 3821.8636 | Phase2_Stabilization | 92.307 | 7.9997 | 64.507 | 53.2324 | 56.6716 | 48.5752 | 135.1612 | 25.1859 | 28.4822 | 414.1777 | 45.7694 | 8.4083 | 32.5839 | 0.86536 | 7.7697 | 7.4284 | 11.3756 | 127 | 7 | 22 | 5
240 | 2026-02-14 17:23 | 54.5186 | 3580.3404 | Phase2_Stabilization | 92.3157 | 7.9372 | 64.3537 | 52.9665 | 56.5193 | 48.8942 | 137.2065 | 25.5047 | 28.7201 | 416.422 | 45.9505 | 8.2617 | 32.1735 | 0.8733 | 6.6505 | 7.2436 | 11.2921 | 127 | 7 | 22 | 5
241 | 2026-02-14 17:23 | 54.7458 | 3701.6505 | Phase3_StableRated | 92.0687 | 7.991 | 64.8017 | 53.4158 | 56.5967 | 48.4415 | 135.2149 | 25.2659 | 28.7882 | 416.0854 | 45.8052 | 8.2982 | 32.2605 | 0.87465 | 6.3141 | 7.5636 | 8.4152 | 127 | 7 | 22 | 5
242 | 2026-02-14 17:24 | 54.973 | 3813.8911 | Phase3_StableRated | 92.0518 | 7.8992 | 65.0367 | 52.8126 | 56.1523 | 48.9401 | 136.5846 | 25.2814 | 28.4746 | 415.3401 | 45.6579 | 8.228 | 32.1138 | 0.86342 | 6.5045 | 7.5071 | 5.9351 | 127 | 7 | 22 | 5
243 | 2026-02-14 17:24 | 55.2001 | 3885.6803 | Phase3_StableRated | 91.7576 | 8.0164 | 64.0837 | 53.3513 | 56.2596 | 48.6306 | 136.9048 | 25.402 | 28.5553 | 415.1789 | 45.536 | 8.3335 | 32.2088 | 0.87623 | 6.3888 | 7.4051 | 10.225 | 127 | 7 | 22 | 5
244 | 2026-02-14 17:24 | 55.4273 | 3578.3777 | Phase3_StableRated | 92.6162 | 7.9885 | 64.631 | 53.1588 | 56.0566 | 48.4763 | 136.3176 | 25.3227 | 28.3239 | 415.1661 | 46.0371 | 8.3968 | 32.1524 | 0.86709 | 7.5725 | 7.5108 | 6.9589 | 127 | 7 | 22 | 5
245 | 2026-02-14 17:24 | 55.6544 | 3729.0569 | Phase3_StableRated | 91.3302 | 7.9126 | 64.7697 | 53.1293 | 56.2167 | 48.5563 | 134.3156 | 25.4813 | 28.621 | 414.4364 | 46.0778 | 8.3252 | 32.2603 | 0.87226 | 5.9669 | 7.4562 | 6.9587 | 127 | 7 | 22 | 5
246 | 2026-02-14 17:24 | 55.8816 | 3722.5521 | Phase3_StableRated | 92.7069 | 8 | 64.1393 | 53.1044 | 56.2726 | 48.6608 | 134.8961 | 25.4265 | 28.6127 | 415.5683 | 46.2285 | 8.2704 | 32.216 | 0.87675 | 6.4119 | 7.2018 | 6.4496 | 127 | 7 | 22 | 5
247 | 2026-02-14 17:25 | 56.1088 | 3710.1208 | Phase3_StableRated | 91.7232 | 7.9184 | 64.7163 | 53.119 | 56.5167 | 48.5026 | 136.8504 | 25.2279 | 28.6713 | 415.6325 | 45.9381 | 8.4122 | 32.2969 | 0.87375 | 5.711 | 7.4888 | 8.6017 | 127 | 7 | 22 | 5
248 | 2026-02-14 17:25 | 56.3359 | 4103.3912 | Phase3_StableRated | 91.1219 | 7.9476 | 64.8821 | 52.7455 | 56.0905 | 48.5421 | 135.4101 | 25.6083 | 28.5731 | 415.749 | 45.639 | 8.2951 | 32.1803 | 0.87362 | 7.3949 | 7.3483 | 11.9384 | 127 | 7 | 22 | 5
249 | 2026-02-14 17:25 | 56.5631 | 3906.3067 | Phase3_StableRated | 91.9006 | 7.939 | 64.0455 | 53.3699 | 56.2435 | 48.5018 | 135.9056 | 25.3967 | 28.9725 | 414.0924 | 45.2633 | 8.3358 | 32.3627 | 0.86941 | 7.7952 | 7.629 | 8.9433 | 127 | 7 | 22 | 5
250 | 2026-02-14 17:26 | 56.7902 | 3661.5169 | Phase3_StableRated | 91.475 | 8.0406 | 64.0662 | 52.986 | 56.4275 | 48.5482 | 136.4252 | 25.2597 | 28.4578 | 414.3656 | 45.8628 | 8.3233 | 32.3907 | 0.86814 | 6.7075 | 7.4511 | 7.7866 | 127 | 7 | 22 | 5
251 | 2026-02-14 17:26 | 57.0174 | 4017.2912 | Phase3_StableRated | 92.5384 | 7.8581 | 64.8145 | 53.1406 | 56.0089 | 48.6794 | 136.2102 | 25.4115 | 28.2928 | 414.4709 | 45.8461 | 8.3415 | 32.1924 | 0.86628 | 6.5985 | 7.8032 | 5.16 | 127 | 7 | 22 | 5
252 | 2026-02-14 17:26 | 57.2446 | 4220.847 | Phase3_StableRated | 91.5867 | 7.9358 | 64.5548 | 53.2199 | 56.3203 | 48.5358 | 136.1942 | 25.329 | 28.5022 | 413.0873 | 45.7613 | 8.3259 | 32.2836 | 0.88223 | 7.3541 | 7.8963 | 10.5879 | 127 | 7 | 22 | 5
253 | 2026-02-14 17:26 | 57.4717 | 4066.0611 | Phase3_StableRated | 91.6785 | 8.0089 | 64.5579 | 52.8721 | 56.0694 | 48.7087 | 135.7042 | 25.3553 | 28.4069 | 413.5552 | 45.8415 | 8.3034 | 32.3722 | 0.87639 | 7.9603 | 7.727 | 6.9394 | 127 | 7 | 22 | 5
254 | 2026-02-14 17:26 | 57.6989 | 3682.8746 | Phase3_StableRated | 91.0268 | 7.9407 | 64.1872 | 53.0181 | 56.2703 | 48.5625 | 135.6053 | 25.6753 | 28.3492 | 415.3606 | 45.454 | 8.3496 | 32.3245 | 0.87371 | 7.2504 | 7.2533 | 9.4554 | 127 | 7 | 22 | 5
255 | 2026-02-14 17:27 | 57.9261 | 3860.0064 | Phase3_StableRated | 91.8902 | 7.9267 | 64.4476 | 52.9816 | 56.1225 | 48.3669 | 136.5798 | 25.3003 | 28.4009 | 415.5887 | 45.9607 | 8.2478 | 32.2604 | 0.87089 | 6.5211 | 7.8775 | 8.2938 | 127 | 7 | 22 | 5
256 | 2026-02-14 17:27 | 58.1532 | 4148.9855 | Phase3_StableRated | 90.7946 | 7.9775 | 64.0462 | 53.0997 | 56.1011 | 48.6352 | 135.98 | 25.3216 | 28.4936 | 414.2365 | 45.9319 | 8.3864 | 32.393 | 0.87015 | 5.6423 | 7.9331 | 10.844 | 127 | 7 | 22 | 5
257 | 2026-02-14 17:27 | 58.3804 | 3855.9715 | Phase3_StableRated | 90.8642 | 7.9233 | 64.8561 | 52.5704 | 56.2329 | 48.7127 | 135.8853 | 25.343 | 28.274 | 413.9291 | 45.772 | 8.3416 | 32.3991 | 0.86748 | 6.4322 | 7.5263 | 9.4049 | 127 | 7 | 22 | 5
258 | 2026-02-14 17:27 | 58.6075 | 4051.2787 | Phase3_StableRated | 92.3227 | 7.9823 | 64.7962 | 53 | 56.2514 | 48.6053 | 136.2996 | 25.4296 | 28.6492 | 415.7002 | 46.0613 | 8.3023 | 32.2912 | 0.87448 | 6.6593 | 7.8807 | 8.5855 | 127 | 7 | 22 | 5
259 | 2026-02-14 17:28 | 58.8347 | 4118.3889 | Phase3_StableRated | 92.3734 | 7.9944 | 64.5706 | 52.8267 | 56.2432 | 48.8955 | 135.9317 | 25.1552 | 28.4221 | 413.1824 | 46.0323 | 8.3249 | 32.2684 | 0.87004 | 6.6871 | 7.4371 | 10.7308 | 127 | 7 | 22 | 5
260 | 2026-02-14 17:28 | 59.0619 | 3868.0227 | Phase3_StableRated | 92.2143 | 7.9334 | 64.151 | 53.2583 | 56.1297 | 48.5649 | 135.2603 | 25.1079 | 28.3648 | 415.4209 | 45.8628 | 8.3135 | 32.2919 | 0.88118 | 7.1919 | 7.1459 | 15.1628 | 127 | 7 | 22 | 5
261 | 2026-02-14 17:28 | 59.289 | 4018.9533 | Phase3_StableRated | 91.3251 | 7.9565 | 63.9062 | 53.2052 | 56.4829 | 48.5236 | 135.2704 | 25.2008 | 28.6691 | 413.0532 | 45.8876 | 8.2832 | 32.2793 | 0.87516 | 6.6481 | 7.4198 | 11.4731 | 127 | 7 | 22 | 5
262 | 2026-02-14 17:28 | 59.5162 | 3537.3696 | Phase3_StableRated | 91.8359 | 7.9714 | 64.5766 | 53.0069 | 56.4611 | 48.4098 | 134.8713 | 25.0954 | 28.4788 | 414.6351 | 45.8119 | 8.254 | 32.305 | 0.87667 | 6.1458 | 7.9496 | 8.746 | 127 | 7 | 22 | 5
263 | 2026-02-14 17:29 | 59.7433 | 3899.1007 | Phase3_StableRated | 91.7153 | 7.9501 | 64.4021 | 53.0366 | 56.3323 | 48.3969 | 135.6405 | 25.2616 | 28.4641 | 414.5812 | 45.8059 | 8.3523 | 32.2773 | 0.86293 | 6.2085 | 7.2591 | 9.3729 | 127 | 7 | 22 | 5
264 | 2026-02-14 17:29 | 59.9705 | 4035.1 | Phase3_StableRated | 91.1928 | 7.9826 | 64.394 | 52.899 | 56.5031 | 48.4466 | 136.876 | 25.3255 | 28.5781 | 414.8577 | 46.0629 | 8.4019 | 32.3157 | 0.867 | 7.9921 | 7.5748 | 7.9093 | 127 | 7 | 22 | 5
265 | 2026-02-14 17:29 | 60.1977 | 3895.0721 | Phase3_StableRated | 92.4595 | 7.9656 | 64.7632 | 52.8778 | 55.9855 | 48.4773 | 135.5317 | 25.1891 | 28.3056 | 414.8059 | 46.0514 | 8.297 | 32.2317 | 0.86308 | 7.8313 | 7.5704 | 6.9799 | 127 | 7 | 22 | 5
266 | 2026-02-14 17:29 | 60.4248 | 4360.4191 | Phase3_StableRated | 92.5012 | 7.9308 | 64.3754 | 53.1982 | 56.2129 | 48.6039 | 136.3814 | 25.1234 | 28.1659 | 413.6772 | 46.4376 | 8.2638 | 32.3787 | 0.88387 | 8.4003 | 7.4364 | 8.2821 | 127 | 7 | 22 | 5
267 | 2026-02-14 17:30 | 60.652 | 3897.4539 | Phase3_StableRated | 91.661 | 7.903 | 64.6701 | 52.9554 | 55.9741 | 48.1794 | 135.3596 | 25.3642 | 28.5622 | 414.1536 | 46.2642 | 8.3365 | 32.2217 | 0.87064 | 7.3695 | 7.4788 | 7.383 | 127 | 7 | 22 | 5
268 | 2026-02-14 17:30 | 60.8791 | 4067.5501 | Phase3_StableRated | 91.7294 | 8.0195 | 63.921 | 52.4768 | 56.1176 | 48.5423 | 135.3471 | 25.3981 | 28.6036 | 414.177 | 45.7246 | 8.3878 | 32.2409 | 0.8736 | 6.4607 | 7.61 | 10.7275 | 127 | 7 | 22 | 5
269 | 2026-02-14 17:30 | 61.1063 | 4172.1459 | Phase3_StableRated | 92.0083 | 7.9397 | 64.2493 | 52.8704 | 56.1977 | 48.5189 | 134.7826 | 25.1936 | 28.7326 | 415.0544 | 45.1549 | 8.3822 | 32.3338 | 0.8686 | 7.9912 | 7.4342 | 6.9003 | 127 | 7 | 22 | 5
270 | 2026-02-14 17:30 | 61.3335 | 4392.2973 | Phase3_StableRated | 90.8107 | 7.867 | 64.3299 | 52.6589 | 56.586 | 48.6222 | 136.0782 | 25.365 | 28.5149 | 413.4034 | 46.1387 | 8.2861 | 32.271 | 0.87097 | 7.2713 | 7.2547 | 13.1047 | 127 | 7 | 22 | 5
271 | 2026-02-14 17:31 | 61.5606 | 3958.2959 | Phase3_StableRated | 91.6261 | 7.9433 | 64.4846 | 52.6103 | 56.5763 | 48.589 | 135.9377 | 25.3946 | 28.5579 | 415.1106 | 45.8121 | 8.3593 | 32.3248 | 0.88522 | 7.31 | 7.5885 | 11.6552 | 127 | 7 | 22 | 5
272 | 2026-02-14 17:31 | 61.7878 | 4379.7218 | Phase3_StableRated | 91.5603 | 7.9301 | 64.1772 | 52.6954 | 56.195 | 48.6094 | 136.5154 | 25.4136 | 28.4197 | 413.9351 | 45.8005 | 8.2795 | 32.2846 | 0.87796 | 7.1095 | 7.7656 | 9.7841 | 127 | 7 | 22 | 5
273 | 2026-02-14 17:31 | 62.015 | 4215.0572 | Phase3_StableRated | 91.2454 | 7.979 | 64.2829 | 52.9866 | 56.0585 | 48.726 | 136.009 | 25.4812 | 28.5306 | 413.2074 | 45.7146 | 8.3516 | 32.3181 | 0.87839 | 5.0093 | 7.7498 | 9.4236 | 127 | 7 | 22 | 5
274 | 2026-02-14 17:31 | 62.2421 | 4075.5719 | Phase3_StableRated | 91.7918 | 7.9084 | 64.5737 | 53.2761 | 56.0992 | 48.4401 | 134.7426 | 25.4912 | 28.7365 | 415.2049 | 45.7454 | 8.2427 | 32.3016 | 0.87083 | 7.9393 | 7.4175 | 7.8614 | 127 | 7 | 22 | 5
275 | 2026-02-14 17:32 | 62.4693 | 4316.5114 | Phase3_StableRated | 92.7941 | 7.9546 | 64.3702 | 52.9653 | 56.2275 | 48.594 | 136.7522 | 25.305 | 28.2316 | 413.1559 | 46.0218 | 8.3043 | 32.3268 | 0.87557 | 7.2889 | 7.3194 | 10.0868 | 127 | 7 | 22 | 5
276 | 2026-02-14 17:32 | 62.6964 | 4290.8554 | Phase3_StableRated | 92.2305 | 7.9816 | 64.008 | 52.7561 | 56.2818 | 48.6774 | 136.0569 | 25.3524 | 28.5852 | 413.4417 | 45.6199 | 8.3104 | 32.2999 | 0.87818 | 7.2098 | 7.5221 | 12.1373 | 127 | 7 | 22 | 5
277 | 2026-02-14 17:32 | 62.9236 | 4181.4349 | Phase3_StableRated | 91.5112 | 7.9929 | 64.9927 | 53.0411 | 55.9706 | 48.755 | 136.0722 | 25.2692 | 28.8158 | 414.1975 | 45.7032 | 8.3167 | 32.2908 | 0.87416 | 6.9722 | 7.9025 | 7.5616 | 127 | 7 | 22 | 5
278 | 2026-02-14 17:33 | 63.1508 | 4301.532 | Phase3_StableRated | 92.0639 | 7.981 | 64.8211 | 52.8378 | 55.9795 | 48.2807 | 135.7796 | 25.3176 | 28.5724 | 414.3727 | 45.8713 | 8.3084 | 32.3367 | 0.88436 | 7.0271 | 7.7203 | 5.367 | 127 | 7 | 22 | 5
279 | 2026-02-14 17:33 | 63.3779 | 4245.8726 | Phase3_StableRated | 92.6346 | 7.9788 | 64.375 | 52.8726 | 56.3478 | 48.4122 | 135.2224 | 25.4258 | 28.684 | 415.1596 | 45.9313 | 8.3417 | 32.3335 | 0.88448 | 6.4218 | 7.7225 | 11.2222 | 127 | 7 | 22 | 5
280 | 2026-02-14 17:33 | 63.6051 | 4339.2286 | Phase3_StableRated | 92.115 | 7.9685 | 64.5551 | 52.6088 | 56.5582 | 48.3627 | 136.0912 | 25.1624 | 28.3984 | 414.9887 | 46.0151 | 8.2812 | 32.2626 | 0.87328 | 7.4206 | 7.7505 | 10.3942 | 127 | 7 | 22 | 5
281 | 2026-02-14 17:33 | 63.8322 | 4440.361 | Phase3_StableRated | 92.1093 | 7.9216 | 64.2717 | 52.6323 | 55.9128 | 48.5825 | 136.062 | 25.1816 | 28.4249 | 413.585 | 45.7969 | 8.2362 | 32.2944 | 0.87658 | 5.9639 | 7.6548 | 6.7072 | 127 | 7 | 22 | 5
282 | 2026-02-14 17:34 | 64.0594 | 4600.1145 | Phase3_StableRated | 91.467 | 7.8752 | 64.4914 | 52.8974 | 56.2774 | 48.5731 | 134.2757 | 25.5039 | 28.5865 | 413.9727 | 45.5883 | 8.3819 | 32.3575 | 0.88504 | 6.9993 | 7.6301 | 7.2517 | 127 | 7 | 22 | 5
283 | 2026-02-14 17:34 | 64.2866 | 4174.4396 | Phase3_StableRated | 92.5485 | 7.9558 | 64.6615 | 52.9785 | 56.188 | 48.5154 | 135.4298 | 25.4087 | 28.2562 | 413.8667 | 45.791 | 8.2871 | 32.361 | 0.8771 | 7.3609 | 7.7244 | 7.1543 | 127 | 7 | 22 | 5
284 | 2026-02-14 17:34 | 64.5137 | 4716.4314 | Phase3_StableRated | 92.1813 | 7.9343 | 64.6402 | 53.0195 | 56.4064 | 48.516 | 136.0142 | 25.2499 | 28.3309 | 412.5436 | 45.9525 | 8.3252 | 32.338 | 0.87209 | 7.135 | 7.4419 | 7.9456 | 127 | 7 | 22 | 5
285 | 2026-02-14 17:34 | 64.7409 | 4093.7314 | Phase3_StableRated | 92.3289 | 7.961 | 64.2292 | 53.001 | 56.3341 | 48.1613 | 136.295 | 25.3755 | 28.3531 | 413.8616 | 46.1483 | 8.3584 | 32.3918 | 0.87818 | 7.3942 | 7.2758 | 8.8361 | 127 | 7 | 22 | 5
286 | 2026-02-14 17:34 | 64.968 | 4390.3894 | Phase3_StableRated | 92.119 | 7.9428 | 64.2563 | 52.7876 | 56.3808 | 48.8064 | 136.9996 | 25.3386 | 28.6524 | 412.5536 | 45.5325 | 8.3515 | 32.3464 | 0.88676 | 6.4376 | 7.7315 | 8.7783 | 127 | 7 | 22 | 5
287 | 2026-02-14 17:35 | 65.1952 | 4521.4341 | Phase3_StableRated | 92.5041 | 8.0549 | 64.3156 | 53.1551 | 56.0874 | 48.3695 | 135.5042 | 25.5077 | 28.5684 | 414.3616 | 45.8184 | 8.2937 | 32.308 | 0.87495 | 6.5682 | 7.8061 | 8.1956 | 127 | 7 | 22 | 5
288 | 2026-02-14 17:35 | 65.4224 | 4488.861 | Phase3_StableRated | 91.6728 | 7.8675 | 64.1253 | 52.6775 | 55.8093 | 48.5838 | 135.4225 | 25.37 | 28.5202 | 412.9176 | 45.5712 | 8.4005 | 32.3309 | 0.86951 | 7.1145 | 7.3467 | 7.64 | 127 | 7 | 22 | 5
289 | 2026-02-14 17:35 | 65.6495 | 4363.1299 | Phase3_StableRated | 92.6344 | 7.9047 | 64.3545 | 53.1318 | 56.3586 | 48.5186 | 135.5883 | 25.4442 | 28.5646 | 413.5995 | 45.6681 | 8.4039 | 32.2905 | 0.87532 | 7.5458 | 7.7299 | 9.1902 | 127 | 7 | 22 | 5
290 | 2026-02-14 17:35 | 65.8767 | 4443.3246 | Phase3_StableRated | 92.1141 | 8.0187 | 63.8755 | 52.8718 | 56.6589 | 48.7039 | 135.5071 | 25.6089 | 28.4794 | 414.8368 | 45.9309 | 8.3214 | 32.3424 | 0.87782 | 5.9931 | 7.9094 | 10.1775 | 127 | 7 | 22 | 5
291 | 2026-02-14 17:36 | 66.1039 | 4414.2579 | Phase3_StableRated | 92.9857 | 7.9475 | 64.6423 | 52.7199 | 56.6182 | 48.0385 | 135.7124 | 25.4123 | 28.7281 | 414.5135 | 45.9825 | 8.338 | 32.1814 | 0.86828 | 7.4316 | 7.5928 | 8.5986 | 127 | 7 | 22 | 5
292 | 2026-02-14 17:36 | 66.331 | 4414.6388 | Phase3_StableRated | 91.7025 | 7.9505 | 64.7426 | 52.6766 | 56.4461 | 48.5338 | 136.3393 | 25.285 | 28.4784 | 415.2847 | 45.8495 | 8.2708 | 32.3334 | 0.87525 | 6.4901 | 7.4184 | 12.4736 | 127 | 7 | 22 | 5
293 | 2026-02-14 17:36 | 66.5582 | 4654.8528 | Phase3_StableRated | 92.679 | 7.8662 | 64.3647 | 52.8607 | 56.4539 | 48.5777 | 135.2391 | 25.4576 | 28.5773 | 413.006 | 45.9742 | 8.3111 | 32.3856 | 0.8757 | 7.0533 | 7.6129 | 10.8045 | 127 | 7 | 22 | 5
294 | 2026-02-14 17:36 | 66.7853 | 4593.3401 | Phase3_StableRated | 91.965 | 7.9414 | 64.4849 | 52.9632 | 56.3848 | 48.5673 | 136.234 | 25.2677 | 28.4896 | 414.3619 | 45.7679 | 8.2897 | 32.2608 | 0.8827 | 6.1093 | 7.4768 | 5.4247 | 127 | 7 | 22 | 5
295 | 2026-02-14 17:37 | 67.0125 | 4444.7659 | Phase3_StableRated | 91.6484 | 7.938 | 64.4156 | 53.2004 | 55.936 | 48.7229 | 134.5449 | 25.5504 | 28.582 | 414.8401 | 45.703 | 8.3281 | 32.2019 | 0.88442 | 6.4999 | 7.4507 | 11.0047 | 127 | 7 | 22 | 5
296 | 2026-02-14 17:37 | 67.2397 | 4708.9646 | Phase3_StableRated | 91.5281 | 8.0007 | 64.5378 | 53.4259 | 56.2377 | 48.4074 | 135.1963 | 25.3163 | 28.4965 | 413.2844 | 46.2522 | 8.3413 | 32.2781 | 0.87481 | 7.4576 | 7.6985 | 10.8221 | 127 | 7 | 22 | 5
297 | 2026-02-14 17:37 | 67.4668 | 4631.8757 | Phase3_StableRated | 91.7386 | 7.9596 | 64.4266 | 53.3968 | 56.6625 | 48.7089 | 135.93 | 25.2921 | 28.5762 | 413.2816 | 45.888 | 8.3199 | 32.2978 | 0.882 | 7.2699 | 7.2249 | 8.8723 | 127 | 7 | 22 | 5
298 | 2026-02-14 17:38 | 67.694 | 4726.2832 | Phase3_StableRated | 92.3516 | 7.95 | 64.6011 | 52.9314 | 56.1792 | 48.5834 | 137.2227 | 25.2189 | 28.3695 | 413.6972 | 46.087 | 8.3302 | 32.3618 | 0.8823 | 6.6965 | 7.2971 | 5.6828 | 127 | 7 | 22 | 5
299 | 2026-02-14 17:38 | 67.9211 | 4713.0944 | Phase3_StableRated | 92.1904 | 7.9377 | 64.5449 | 52.9831 | 56.7339 | 48.8428 | 135.6583 | 25.4448 | 28.3736 | 414.4838 | 45.8273 | 8.2847 | 32.1662 | 0.86612 | 6.9214 | 7.5942 | 9.5791 | 127 | 7 | 22 | 5
300 | 2026-02-14 17:38 | 68.1483 | 4500.6777 | Phase3_StableRated | 91.5361 | 7.9652 | 64.1178 | 52.9053 | 56.0936 | 48.4131 | 133.7983 | 25.4589 | 28.7178 | 413.699 | 45.563 | 8.3005 | 32.2354 | 0.87721 | 7.1214 | 7.6291 | 9.0109 | 127 | 7 | 22 | 5
301 | 2026-02-14 17:38 | 68.3755 | 4558.1028 | Phase3_StableRated | 92.0635 | 7.9351 | 64.6869 | 53.267 | 56.4595 | 48.3769 | 134.2382 | 25.2414 | 28.4798 | 415.3145 | 45.4642 | 8.2941 | 32.3781 | 0.87762 | 7.3032 | 7.6541 | 6.7996 | 127 | 7 | 22 | 5
302 | 2026-02-14 17:38 | 68.6026 | 4777.7764 | Phase3_StableRated | 92.8535 | 7.9412 | 64.6656 | 52.7005 | 55.9122 | 48.6621 | 135.8825 | 25.3943 | 28.4686 | 413.8028 | 45.6702 | 8.3252 | 32.3594 | 0.87649 | 6.9221 | 7.9812 | 5.8087 | 127 | 7 | 22 | 5
303 | 2026-02-14 17:39 | 68.8298 | 4771.8217 | Phase3_StableRated | 92.7601 | 8.0042 | 64.2814 | 53.0382 | 56.4358 | 48.465 | 136.3187 | 25.1302 | 28.5678 | 411.7637 | 45.9996 | 8.3295 | 32.2206 | 0.88246 | 7.6528 | 7.6014 | 9.52 | 127 | 7 | 22 | 5
304 | 2026-02-14 17:39 | 69.0569 | 4688.645 | Phase3_StableRated | 92.3006 | 7.9383 | 64.4516 | 53.2786 | 55.9043 | 48.4136 | 136.6217 | 25.2896 | 28.3858 | 414.487 | 46.161 | 8.2686 | 32.4047 | 0.88375 | 7.9671 | 7.6793 | 9.4518 | 127 | 7 | 22 | 5
305 | 2026-02-14 17:39 | 69.2841 | 4725.6716 | Phase3_StableRated | 91.8197 | 7.9928 | 64.6483 | 53.4061 | 56.0761 | 48.4213 | 136.3716 | 25.3399 | 28.5269 | 414.5076 | 45.9374 | 8.3118 | 32.3043 | 0.86879 | 7.5407 | 7.3843 | 8.6498 | 127 | 7 | 22 | 5
306 | 2026-02-14 17:40 | 69.5113 | 4922.361 | Phase3_StableRated | 92.0188 | 8.0084 | 64.3947 | 52.8456 | 56.2891 | 48.736 | 136.7416 | 25.5273 | 28.7915 | 414.8844 | 45.6393 | 8.3812 | 32.2848 | 0.87764 | 6.9427 | 7.7822 | 9.0139 | 127 | 7 | 22 | 5
307 | 2026-02-14 17:40 | 69.7384 | 4645.8029 | Phase3_StableRated | 92.2281 | 8.0087 | 64.678 | 53.0481 | 56.4028 | 48.7782 | 135.8262 | 25.2276 | 28.7874 | 415.7378 | 46.1142 | 8.3501 | 32.2804 | 0.8774 | 7.7367 | 7.4838 | 6.8315 | 127 | 7 | 22 | 5
308 | 2026-02-14 17:40 | 69.9656 | 4839.1074 | Phase3_StableRated | 91.625 | 7.8724 | 65.0027 | 53.4946 | 56.0503 | 48.4108 | 136.5651 | 25.1591 | 28.6492 | 413.9446 | 45.7694 | 8.3459 | 32.2204 | 0.88124 | 7.15 | 7.595 | 8.6982 | 127 | 7 | 22 | 5
309 | 2026-02-14 17:40 | 70.1927 | 4737.4953 | Phase3_StableRated | 91.5768 | 7.9773 | 64.2317 | 52.8558 | 56.0924 | 48.1521 | 134.2789 | 25.2416 | 28.4325 | 414.3342 | 45.9053 | 8.3084 | 32.3644 | 0.88132 | 7.5016 | 7.575 | 10.9768 | 127 | 7 | 22 | 5
310 | 2026-02-14 17:40 | 70.4199 | 4750.5097 | Phase3_StableRated | 90.9768 | 7.9188 | 64.0193 | 52.682 | 56.2194 | 48.5452 | 135.068 | 25.1359 | 28.6171 | 414.9369 | 45.8111 | 8.3413 | 32.3195 | 0.88312 | 7.5394 | 7.7963 | 8.8915 | 127 | 7 | 22 | 5
311 | 2026-02-14 17:41 | 70.6471 | 4971.5866 | Phase3_StableRated | 92.0874 | 7.9076 | 64.6843 | 52.7476 | 56.2329 | 48.2528 | 134.6126 | 25.4623 | 28.3968 | 413.6344 | 45.7767 | 8.3285 | 32.2725 | 0.87607 | 6.5125 | 7.317 | 5.51 | 127 | 7 | 22 | 5
312 | 2026-02-14 17:41 | 70.8742 | 4944.3191 | Phase3_StableRated | 92.3239 | 7.9385 | 64.711 | 53.1959 | 56.3531 | 48.315 | 135.8621 | 25.4965 | 28.466 | 414.4538 | 46.1089 | 8.4181 | 32.3488 | 0.87779 | 6.4448 | 7.1362 | 8.3568 | 127 | 7 | 22 | 5
313 | 2026-02-14 17:41 | 71.1014 | 4957.8931 | Phase3_StableRated | 91.765 | 7.9974 | 64.2391 | 52.544 | 56.5504 | 48.0763 | 135.7005 | 25.4541 | 28.2679 | 414.3493 | 45.75 | 8.302 | 32.2271 | 0.87339 | 6.4206 | 7.5781 | 6.6246 | 127 | 7 | 22 | 5
314 | 2026-02-14 17:42 | 71.3286 | 5050.1771 | Phase3_StableRated | 92.8181 | 7.9265 | 64.942 | 52.9131 | 56.3548 | 48.7315 | 135.9913 | 25.4427 | 28.753 | 414.9944 | 45.4751 | 8.3621 | 32.2178 | 0.88145 | 7.6461 | 7.6994 | 10.2914 | 127 | 7 | 22 | 5
315 | 2026-02-14 17:42 | 71.5557 | 4864.9641 | Phase3_StableRated | 91.5124 | 7.9404 | 64.0856 | 53.158 | 56.6956 | 48.562 | 136.1492 | 25.2993 | 28.4196 | 414.2429 | 45.865 | 8.3466 | 32.2832 | 0.87505 | 6.127 | 7.6235 | 10.5748 | 127 | 7 | 22 | 5
316 | 2026-02-14 17:42 | 71.7829 | 4983.6444 | Phase3_StableRated | 91.2787 | 8.0498 | 64.7252 | 53.0695 | 56.4664 | 48.6025 | 134.8647 | 25.2953 | 28.393 | 414.5481 | 45.7974 | 8.3508 | 32.2665 | 0.87205 | 7.0615 | 7.8386 | 5.6103 | 127 | 7 | 22 | 5
317 | 2026-02-14 17:42 | 72.01 | 4844.0844 | Phase3_StableRated | 91.8671 | 7.9399 | 64.2529 | 53.1478 | 56.3805 | 48.7718 | 135.8043 | 25.3178 | 28.2276 | 413.8051 | 46.4735 | 8.3795 | 32.2842 | 0.87712 | 7.2962 | 7.642 | 12.2279 | 127 | 7 | 22 | 5
318 | 2026-02-14 17:42 | 72.2372 | 4958.6227 | Phase3_StableRated | 92.2737 | 8.0605 | 64.9745 | 53.0828 | 56.0695 | 48.7534 | 134.7065 | 25.3088 | 28.6064 | 416.0058 | 45.9408 | 8.3498 | 32.2561 | 0.86369 | 7.817 | 7.4818 | 6.8936 | 127 | 7 | 22 | 5
319 | 2026-02-14 17:43 | 72.4644 | 4903.0892 | Phase3_StableRated | 92.7435 | 7.9144 | 65.0688 | 53.2687 | 56.3348 | 49.0018 | 137.1735 | 25.2405 | 28.3914 | 414.9628 | 45.8193 | 8.3847 | 32.4186 | 0.87016 | 7.2331 | 7.0973 | 14.0319 | 127 | 7 | 22 | 5
320 | 2026-02-14 17:43 | 72.6915 | 4954.0044 | Phase3_StableRated | 91.6328 | 7.99 | 64.1393 | 53.1367 | 56.2585 | 48.4297 | 135.8375 | 25.4526 | 28.3588 | 415.8174 | 45.5738 | 8.3071 | 32.1765 | 0.86988 | 6.2753 | 7.5462 | 9.674 | 127 | 7 | 22 | 5
321 | 2026-02-14 17:43 | 72.9187 | 5047.2557 | Phase3_StableRated | 92.4484 | 7.9188 | 64.4333 | 52.8457 | 56.5176 | 48.655 | 135.5248 | 25.3727 | 28.5355 | 416.1701 | 45.539 | 8.398 | 32.2365 | 0.87485 | 6.4035 | 7.8015 | 6.6766 | 127 | 7 | 22 | 5
322 | 2026-02-14 17:44 | 73.1458 | 4841.9069 | Phase3_StableRated | 92.0925 | 7.9043 | 64.6642 | 52.9947 | 56.6055 | 48.314 | 137.1556 | 25.4159 | 28.3862 | 415.8255 | 45.8926 | 8.3738 | 32.2769 | 0.8692 | 6.175 | 7.5416 | 6.5678 | 127 | 7 | 22 | 5
323 | 2026-02-14 17:44 | 73.373 | 5312.0048 | Phase3_StableRated | 91.7731 | 7.9211 | 64.2841 | 53.2677 | 56.078 | 48.4561 | 135.2046 | 25.3988 | 28.3959 | 415.028 | 45.9044 | 8.3205 | 32.2281 | 0.8728 | 6.9232 | 7.588 | 10.8904 | 127 | 7 | 22 | 5
324 | 2026-02-14 17:44 | 73.6002 | 4843.4391 | Phase3_StableRated | 92.5863 | 7.9945 | 64.468 | 53.2528 | 56.3979 | 48.5264 | 134.5628 | 25.319 | 28.2137 | 415.1138 | 46.0244 | 8.4171 | 32.2656 | 0.87987 | 6.5744 | 7.7054 | 8.5532 | 127 | 7 | 22 | 5
325 | 2026-02-14 17:44 | 73.8273 | 4826.3547 | Phase3_StableRated | 92.4743 | 7.9283 | 64.554 | 53.2531 | 56.7315 | 48.6059 | 135.1015 | 25.2862 | 28.3472 | 417.2835 | 46.0928 | 8.3008 | 32.291 | 0.87165 | 6.3333 | 7.3948 | 9.521 | 127 | 7 | 22 | 5
326 | 2026-02-14 17:44 | 74.0545 | 5212.3639 | Phase3_StableRated | 91.1489 | 7.9934 | 63.8095 | 53.4499 | 56.6894 | 48.6014 | 136.0946 | 25.2996 | 28.6214 | 414.4996 | 45.9669 | 8.3654 | 32.2028 | 0.87024 | 8.1721 | 7.741 | 13.7817 | 127 | 7 | 22 | 5
327 | 2026-02-14 17:45 | 74.2816 | 5170.5552 | Phase3_StableRated | 92.6572 | 7.9441 | 64.7189 | 52.9336 | 56.5964 | 48.8533 | 136.5869 | 25.423 | 28.2651 | 414.6704 | 45.8503 | 8.3105 | 32.2505 | 0.87672 | 6.3939 | 7.9253 | 8.1748 | 127 | 7 | 22 | 5
328 | 2026-02-14 17:45 | 74.5088 | 5159.8173 | Phase3_StableRated | 92.8814 | 7.9071 | 64.4424 | 53.394 | 56.5306 | 48.8538 | 136.6381 | 25.2527 | 28.4232 | 416.0518 | 45.8662 | 8.345 | 32.221 | 0.87549 | 7.9879 | 7.5909 | 9.6729 | 127 | 7 | 22 | 5
329 | 2026-02-14 17:45 | 74.736 | 5175.9113 | Phase3_StableRated | 91.5201 | 8.0485 | 64.3207 | 53.4416 | 56.5107 | 49.0044 | 138.5204 | 25.4091 | 28.4817 | 415.7544 | 45.7632 | 8.3882 | 32.2382 | 0.86361 | 8.1599 | 7.3411 | 13.8365 | 127 | 7 | 22 | 5
330 | 2026-02-14 17:46 | 74.9631 | 5091.2788 | Phase3_StableRated | 92.2531 | 7.9592 | 64.9385 | 53.2211 | 56.4023 | 48.5843 | 133.8202 | 25.3723 | 28.4117 | 416.4569 | 46.1679 | 8.3061 | 32.1882 | 0.87368 | 7.4391 | 7.5966 | 10.4407 | 127 | 7 | 22 | 5
331 | 2026-02-14 17:46 | 75.1903 | 4968.4663 | Phase3_StableRated | 92.2756 | 7.972 | 64.3891 | 53.4589 | 56.6641 | 48.5005 | 136.8025 | 25.2437 | 28.7926 | 414.2477 | 46.0685 | 8.3524 | 32.2341 | 0.87461 | 6.8624 | 7.1351 | 5.8913 | 127 | 7 | 22 | 5
332 | 2026-02-14 17:46 | 75.4175 | 5135.9011 | Phase3_StableRated | 92.3106 | 7.9366 | 64.7151 | 52.8813 | 56.1952 | 48.7009 | 135.4658 | 25.3593 | 28.7894 | 414.9361 | 45.6745 | 8.3233 | 32.1703 | 0.87615 | 7.2574 | 7.6854 | 10.9957 | 127 | 7 | 22 | 5
333 | 2026-02-14 17:46 | 75.6446 | 5033.7146 | Phase3_StableRated | 91.75 | 7.9501 | 64.4531 | 53.1548 | 56.1635 | 48.5341 | 135.8275 | 25.3556 | 28.4718 | 415.9094 | 45.4228 | 8.3525 | 32.1971 | 0.86157 | 6.4964 | 7.6976 | 6.8842 | 127 | 7 | 22 | 5
334 | 2026-02-14 17:46 | 75.8718 | 5307.2503 | Phase3_StableRated | 91.6383 | 7.9617 | 64.6637 | 52.9304 | 56.3086 | 48.9447 | 135.3205 | 25.2015 | 28.623 | 414.9033 | 45.7835 | 8.3067 | 32.2516 | 0.87758 | 7.5577 | 7.9663 | 13.2497 | 127 | 7 | 22 | 5
335 | 2026-02-14 17:47 | 76.0989 | 5147.3897 | Phase3_StableRated | 92.133 | 7.9644 | 64.9032 | 53.316 | 56.3613 | 48.7358 | 135.0241 | 25.4446 | 28.6519 | 417.3997 | 45.9582 | 8.2809 | 32.1908 | 0.87087 | 6.8671 | 7.5875 | 7.5025 | 127 | 7 | 22 | 5
336 | 2026-02-14 17:47 | 76.3261 | 5056.845 | Phase3_StableRated | 92.5431 | 7.9391 | 64.5291 | 52.8643 | 56.701 | 48.4531 | 137.3443 | 25.2423 | 28.405 | 415.4528 | 45.6574 | 8.3357 | 32.2028 | 0.88415 | 6.7685 | 7.6846 | 17.5482 | 127 | 7 | 22 | 5
337 | 2026-02-14 17:47 | 76.5533 | 5151.0258 | Phase3_StableRated | 92.3601 | 7.9828 | 64.8028 | 53.3671 | 56.4424 | 48.4069 | 136.9124 | 25.5259 | 28.4314 | 415.0552 | 45.7959 | 8.3651 | 32.1937 | 0.88065 | 6.4469 | 7.4474 | 13.43 | 127 | 7 | 22 | 5
338 | 2026-02-14 17:48 | 76.7804 | 5281.1669 | Phase3_StableRated | 91.8228 | 7.9741 | 64.9509 | 53.4187 | 55.8591 | 48.7918 | 135.7884 | 25.6863 | 28.539 | 415.9312 | 45.8738 | 8.3174 | 32.2766 | 0.87995 | 5.2765 | 7.5533 | 7.6239 | 127 | 7 | 22 | 5
339 | 2026-02-14 17:48 | 77.0076 | 5144.0381 | Phase3_StableRated | 92.4047 | 7.9836 | 64.5174 | 53.4361 | 56.4605 | 48.5351 | 137.0686 | 25.286 | 28.5568 | 416.6196 | 45.5606 | 8.4302 | 32.1929 | 0.87079 | 6.3573 | 7.315 | 9.7109 | 127 | 7 | 22 | 5
340 | 2026-02-14 17:48 | 77.2347 | 5119.0925 | Phase3_StableRated | 90.296 | 8.0195 | 64.5216 | 53.3317 | 56.8059 | 48.5285 | 134.6505 | 25.4335 | 28.5189 | 417.4561 | 45.9393 | 8.3339 | 32.2101 | 0.87966 | 7.7494 | 7.5889 | 11.5866 | 127 | 7 | 22 | 5
341 | 2026-02-14 17:48 | 77.4619 | 5301.0311 | Phase3_StableRated | 92.5998 | 8.0024 | 64.2014 | 53.0751 | 56.5342 | 48.9928 | 135.2482 | 25.2739 | 28.7321 | 416.7349 | 45.7884 | 8.2574 | 32.2783 | 0.87604 | 7.1049 | 7.568 | 11.6555 | 127 | 7 | 22 | 5
342 | 2026-02-14 17:49 | 77.6891 | 5316.6649 | Phase3_StableRated | 90.949 | 7.982 | 64.626 | 52.976 | 56.6531 | 48.5393 | 133.8768 | 25.4596 | 28.3857 | 415.6678 | 45.9127 | 8.3681 | 32.21 | 0.87567 | 6.7352 | 7.6793 | 10.9545 | 127 | 7 | 22 | 5
343 | 2026-02-14 17:49 | 77.9162 | 5214.6435 | Phase3_StableRated | 91.8992 | 7.9782 | 65.3597 | 53.5169 | 56.3935 | 48.7385 | 135.2867 | 25.2638 | 28.4235 | 416.4881 | 45.5524 | 8.4023 | 32.1697 | 0.87225 | 7.4153 | 7.5046 | 12.8591 | 127 | 7 | 22 | 5
344 | 2026-02-14 17:49 | 78.1434 | 5235.6861 | Phase3_StableRated | 91.7836 | 7.9753 | 64.8328 | 53.3481 | 56.209 | 48.7907 | 136.0129 | 25.4755 | 28.667 | 416.9754 | 45.8827 | 8.3763 | 32.2088 | 0.87791 | 8.1772 | 7.6704 | 9.0967 | 127 | 7 | 22 | 5
345 | 2026-02-14 17:49 | 78.3705 | 5360.9489 | Phase3_StableRated | 91.306 | 7.9621 | 64.2549 | 53.2206 | 56.5017 | 48.315 | 136.2842 | 25.2657 | 28.51 | 416.2813 | 46.2273 | 8.4064 | 32.2198 | 0.87357 | 8.114 | 7.5175 | 9.3283 | 127 | 7 | 22 | 5
346 | 2026-02-14 17:50 | 78.5977 | 5113.9303 | Phase3_StableRated | 92.7573 | 7.9754 | 64.0535 | 53.0245 | 56.1904 | 48.7815 | 136.156 | 25.3222 | 28.4015 | 417.9525 | 45.8859 | 8.3137 | 32.0952 | 0.86578 | 6.4716 | 7.5526 | 8.9612 | 127 | 7 | 22 | 5
347 | 2026-02-14 17:50 | 78.8249 | 5135.7095 | Phase3_StableRated | 91.9262 | 8.0315 | 64.6501 | 52.8787 | 56.9279 | 48.6071 | 134.9154 | 25.2535 | 28.7008 | 416.1983 | 45.6384 | 8.4008 | 32.1598 | 0.86956 | 5.8836 | 7.6406 | 12.0132 | 127 | 7 | 22 | 5
348 | 2026-02-14 17:50 | 79.052 | 5258.7747 | Phase3_StableRated | 92.0284 | 7.8722 | 64.6327 | 53.1078 | 56.6645 | 48.8564 | 136.6906 | 25.4879 | 28.3628 | 415.3881 | 46.0178 | 8.3622 | 32.1415 | 0.88324 | 8.6536 | 7.6408 | 10.6608 | 127 | 7 | 22 | 5
349 | 2026-02-14 17:50 | 79.2792 | 5353.0938 | Phase3_StableRated | 92.1051 | 7.9603 | 64.8789 | 53.5928 | 56.2251 | 48.4121 | 136.2327 | 25.2862 | 28.4491 | 417.1238 | 45.6641 | 8.3631 | 32.2046 | 0.86425 | 8.6039 | 7.7703 | 10.7139 | 127 | 7 | 22 | 5
350 | 2026-02-14 17:50 | 79.5063 | 5450.4368 | Phase3_StableRated | 92.2272 | 7.9423 | 64.7795 | 53.0211 | 56.244 | 48.892 | 136.81 | 25.4612 | 28.5985 | 417.0111 | 46.1229 | 8.3489 | 32.1673 | 0.87272 | 7.366 | 7.6092 | 11.772 | 127 | 7 | 22 | 5
351 | 2026-02-14 17:51 | 79.7335 | 5647.7684 | Phase3_StableRated | 92.0024 | 7.9337 | 64.6756 | 53.1363 | 56.5318 | 48.95 | 134.2568 | 25.3339 | 28.446 | 415.0985 | 45.8864 | 8.2908 | 32.0556 | 0.86739 | 6.1228 | 7.5557 | 4.5865 | 127 | 7 | 22 | 5
352 | 2026-02-14 17:51 | 79.9607 | 5566.7124 | Phase3_StableRated | 91.4872 | 8.0209 | 64.8599 | 53.5747 | 56.4977 | 48.8935 | 136.2827 | 25.3784 | 28.589 | 417.0338 | 45.1298 | 8.3016 | 32.107 | 0.87506 | 7.738 | 7.6157 | 10.3242 | 127 | 7 | 22 | 5
353 | 2026-02-14 17:51 | 80.1878 | 5423.188 | Phase3_StableRated | 92.4688 | 7.95 | 64.5947 | 53.1987 | 56.7567 | 48.8003 | 135.2084 | 25.4866 | 28.8349 | 415.8099 | 45.651 | 8.3029 | 32.2299 | 0.87107 | 7.1736 | 7.4782 | 10.4543 | 127 | 7 | 22 | 5
354 | 2026-02-14 17:51 | 80.415 | 5460.6353 | Phase3_StableRated | 91.7028 | 7.9468 | 64.1391 | 53.437 | 56.452 | 48.6249 | 135.5078 | 25.306 | 28.4237 | 416.5503 | 45.9612 | 8.3785 | 32.1235 | 0.87208 | 6.8862 | 7.5568 | 14.105 | 127 | 7 | 22 | 5
355 | 2026-02-14 17:52 | 80.6422 | 5322.4353 | Phase3_StableRated | 91.3431 | 7.9719 | 64.5992 | 53.4269 | 56.408 | 48.6419 | 136.198 | 25.4494 | 28.9923 | 416.4274 | 45.8972 | 8.4574 | 32.1534 | 0.87726 | 7.4793 | 8.0888 | 5.4204 | 127 | 7 | 22 | 5
356 | 2026-02-14 17:52 | 80.8693 | 5491.5817 | Phase3_StableRated | 92.0118 | 7.978 | 64.7435 | 53.3166 | 56.9458 | 49.0159 | 136.3044 | 25.672 | 28.6735 | 416.3496 | 45.6317 | 8.3225 | 32.1516 | 0.87417 | 7.4859 | 7.4446 | 13.8337 | 127 | 7 | 22 | 5
357 | 2026-02-14 17:52 | 81.0965 | 5464.8164 | Phase3_StableRated | 92.8351 | 8.0132 | 64.8941 | 53.6521 | 56.3672 | 48.6757 | 135.0214 | 25.3396 | 28.6466 | 416.9853 | 45.726 | 8.3854 | 32.1176 | 0.85974 | 6.0964 | 7.6073 | 9.6495 | 127 | 7 | 22 | 5
358 | 2026-02-14 17:52 | 81.3236 | 5575.7531 | Phase3_StableRated | 92.589 | 8.0846 | 65.4459 | 53.018 | 56.5564 | 48.618 | 136.1697 | 25.506 | 28.7165 | 417.1726 | 45.5206 | 8.3516 | 32.2394 | 0.86667 | 7.0023 | 7.5668 | 10.9475 | 127 | 7 | 22 | 5
359 | 2026-02-14 17:53 | 81.5508 | 5411.5542 | Phase3_StableRated | 91.6545 | 7.9414 | 64.797 | 53.7695 | 56.4701 | 48.8926 | 134.7509 | 25.572 | 28.9225 | 416.6224 | 45.6943 | 8.2567 | 32.1998 | 0.87386 | 7.5442 | 7.5875 | 14.1007 | 127 | 7 | 22 | 5
360 | 2026-02-14 17:53 | 81.778 | 5637.336 | Phase3_StableRated | 91.8547 | 8.0029 | 64.3871 | 53.2627 | 56.5518 | 48.5693 | 136.5731 | 25.3007 | 28.4573 | 416.7709 | 46.3194 | 8.2682 | 32.0858 | 0.86814 | 7.1168 | 7.5925 | 10.9843 | 127 | 7 | 22 | 5
361 | 2026-02-14 17:53 | 82.0051 | 5811.0713 | Phase3_StableRated | 91.9535 | 7.9502 | 65.0817 | 53.6398 | 56.7242 | 48.5276 | 136.0195 | 25.2937 | 28.4907 | 417.6462 | 46.0226 | 8.3344 | 32.1795 | 0.87475 | 7.4095 | 7.6995 | 10.8152 | 127 | 7 | 22 | 5
362 | 2026-02-14 17:54 | 82.2323 | 5570.0878 | Phase3_StableRated | 93.0111 | 7.9708 | 65.0867 | 53.4731 | 56.3078 | 48.5574 | 137.2252 | 25.4669 | 28.5936 | 416.802 | 46.2874 | 8.349 | 32.2054 | 0.86893 | 7.9297 | 7.301 | 10.3069 | 127 | 7 | 22 | 5
363 | 2026-02-14 17:54 | 82.4594 | 5665.2621 | Phase3_StableRated | 92.3545 | 7.9495 | 64.8794 | 53.1845 | 56.886 | 48.6678 | 135.7328 | 25.3462 | 28.6476 | 417.6188 | 45.9012 | 8.3019 | 32.17 | 0.87317 | 6.9851 | 7.8587 | 8.5345 | 127 | 7 | 22 | 5
364 | 2026-02-14 17:54 | 82.6866 | 5725.7519 | Phase3_StableRated | 92.328 | 7.9727 | 65.0011 | 53.361 | 57.0259 | 48.7847 | 135.4045 | 25.6187 | 28.3678 | 417.6023 | 45.9914 | 8.3432 | 32.1032 | 0.86658 | 7.0791 | 7.7815 | 9.6415 | 127 | 7 | 22 | 5
365 | 2026-02-14 17:54 | 82.9138 | 5570.7045 | Phase3_StableRated | 92.6429 | 7.9577 | 65.2311 | 53.094 | 56.4154 | 48.7194 | 135.0548 | 25.4325 | 28.7192 | 417.949 | 46.1649 | 8.3358 | 32.2261 | 0.8748 | 4.6255 | 7.438 | 7.3862 | 127 | 7 | 22 | 5
366 | 2026-02-14 17:54 | 83.1409 | 5683.8181 | Phase3_StableRated | 92.3684 | 7.9121 | 64.5139 | 53.5738 | 56.3235 | 48.8835 | 136.4126 | 25.4083 | 28.8086 | 415.6209 | 45.7593 | 8.3168 | 32.0739 | 0.86189 | 6.5397 | 7.1951 | 9.5216 | 127 | 7 | 22 | 5
367 | 2026-02-14 17:55 | 83.3681 | 5666.2137 | Phase3_StableRated | 92.1237 | 8.0039 | 64.842 | 53.464 | 56.7327 | 48.9486 | 135.3944 | 25.3339 | 28.6291 | 418.0475 | 45.8154 | 8.3663 | 31.975 | 0.8657 | 7.5783 | 7.4495 | 3.8065 | 127 | 7 | 22 | 5
368 | 2026-02-14 17:55 | 83.5952 | 5694.9385 | Phase3_StableRated | 91.7868 | 8.0117 | 64.6191 | 53.5197 | 56.7459 | 48.8718 | 136.6508 | 25.525 | 28.5763 | 416.2815 | 46.0204 | 8.3701 | 32.0618 | 0.86468 | 6.9184 | 7.595 | 10.9552 | 127 | 7 | 22 | 5
369 | 2026-02-14 17:55 | 83.8224 | 5574.3632 | Phase3_StableRated | 91.9382 | 8.0182 | 64.7989 | 53.6558 | 56.6686 | 48.7741 | 135.855 | 25.3245 | 28.547 | 418.0281 | 46.0934 | 8.4233 | 32.0732 | 0.86758 | 6.9173 | 8.1746 | 9.5515 | 127 | 7 | 22 | 5
370 | 2026-02-14 17:55 | 84.0496 | 5714.3772 | Phase3_StableRated | 92.1375 | 8.0517 | 64.4837 | 53.4621 | 56.6567 | 48.8763 | 134.2485 | 25.4721 | 28.7767 | 418.6907 | 45.7308 | 8.385 | 32.1238 | 0.87116 | 6.322 | 7.7809 | 8.717 | 127 | 7 | 22 | 5
371 | 2026-02-14 17:56 | 84.2767 | 5803.7743 | Phase3_StableRated | 92.412 | 8.0671 | 64.5842 | 53.354 | 56.6204 | 48.9203 | 135.8351 | 25.5234 | 28.5598 | 418.6721 | 45.756 | 8.372 | 32.0422 | 0.87354 | 7.9911 | 7.279 | 10.4032 | 127 | 7 | 22 | 5
372 | 2026-02-14 17:56 | 84.5039 | 5968.0984 | Phase3_StableRated | 92.4058 | 7.9329 | 64.7963 | 53.2406 | 57.0225 | 48.8795 | 134.8204 | 25.3716 | 28.8397 | 418.011 | 45.8602 | 8.3139 | 32.1116 | 0.86719 | 7.2938 | 7.5187 | 6.0582 | 127 | 7 | 22 | 5
373 | 2026-02-14 17:56 | 84.7311 | 5906.6972 | Phase3_StableRated | 92.6305 | 7.9357 | 64.7705 | 53.2779 | 56.816 | 48.8906 | 136.3508 | 25.3996 | 28.8559 | 417.2558 | 45.9685 | 8.4133 | 32.064 | 0.87689 | 7.8827 | 7.6225 | 15.0052 | 127 | 7 | 22 | 5
374 | 2026-02-14 17:56 | 84.9582 | 6108.6312 | Phase3_StableRated | 91.9207 | 7.9005 | 65.2926 | 53.6295 | 56.4727 | 48.6385 | 134.6849 | 25.5305 | 28.726 | 418.1457 | 45.9975 | 8.3742 | 32.1065 | 0.87701 | 5.6992 | 7.7448 | 9.0815 | 127 | 7 | 22 | 5
375 | 2026-02-14 17:57 | 85.1854 | 5667.8512 | Phase3_StableRated | 92.015 | 7.9801 | 64.7334 | 53.8285 | 56.763 | 48.7681 | 137.0048 | 25.5426 | 28.6913 | 417.3395 | 45.5262 | 8.4283 | 32.1126 | 0.87174 | 7.1633 | 7.3934 | 9.3585 | 127 | 7 | 22 | 5
376 | 2026-02-14 17:57 | 85.4125 | 5939.4165 | Phase3_StableRated | 90.8596 | 7.9431 | 64.7907 | 53.5737 | 57.0498 | 48.9695 | 135.82 | 25.522 | 28.7388 | 418.9028 | 46.0941 | 8.3356 | 32.1187 | 0.86967 | 6.8205 | 7.6312 | 7.3262 | 127 | 7 | 22 | 5
377 | 2026-02-14 17:57 | 85.6397 | 5847.2256 | Phase3_StableRated | 92.6249 | 7.9541 | 64.427 | 53.5884 | 57.3753 | 48.8705 | 135.9119 | 25.4494 | 28.8542 | 418.7738 | 45.7432 | 8.3434 | 32.0126 | 0.85948 | 6.95 | 7.5313 | 9.628 | 127 | 7 | 22 | 5
378 | 2026-02-14 17:58 | 85.8669 | 6176.0873 | Phase3_StableRated | 92.1838 | 8.0393 | 64.7412 | 53.4652 | 56.5081 | 48.9519 | 136.7253 | 25.4473 | 28.5434 | 418.9876 | 45.7335 | 8.3742 | 32.0962 | 0.87839 | 6.8213 | 7.4299 | 13.4056 | 127 | 7 | 22 | 5
379 | 2026-02-14 17:58 | 86.094 | 5723.19 | Phase3_StableRated | 92.5143 | 8.035 | 64.8218 | 53.5514 | 56.4622 | 48.882 | 136.9413 | 25.4245 | 28.6095 | 418.2673 | 45.6548 | 8.3488 | 32.0373 | 0.85832 | 6.9666 | 7.7201 | 12.3897 | 127 | 7 | 22 | 5
380 | 2026-02-14 17:58 | 86.3212 | 5733.7152 | Phase3_StableRated | 90.402 | 8.0436 | 64.7307 | 53.6784 | 56.27 | 48.9713 | 135.7948 | 25.2912 | 28.5038 | 417.221 | 46.1414 | 8.3625 | 32.071 | 0.86709 | 7.4964 | 7.8435 | 11.7146 | 127 | 7 | 22 | 5
381 | 2026-02-14 17:58 | 86.5483 | 5786.6908 | Phase3_StableRated | 93.3217 | 7.9676 | 65.4971 | 53.9348 | 56.6866 | 48.7438 | 135.2051 | 25.4773 | 28.7332 | 418.6963 | 45.8476 | 8.369 | 32.0537 | 0.86073 | 5.7103 | 7.8567 | 10.9478 | 127 | 7 | 22 | 5
382 | 2026-02-14 17:58 | 86.7755 | 5563.9832 | Phase3_StableRated | 91.9186 | 7.9781 | 64.9753 | 53.5295 | 56.5359 | 49.0214 | 134.6769 | 25.7474 | 28.7303 | 418.5648 | 45.4948 | 8.4005 | 32.1361 | 0.86362 | 8.3789 | 7.776 | 8.9721 | 127 | 7 | 22 | 5
383 | 2026-02-14 17:59 | 87.0027 | 5829.0615 | Phase3_StableRated | 92.5464 | 8.0265 | 64.6685 | 53.4233 | 57.0591 | 48.9375 | 135.2171 | 25.3545 | 28.4956 | 419.9214 | 45.8844 | 8.3447 | 32.0261 | 0.87607 | 7.2395 | 7.5848 | 5.8389 | 127 | 7 | 22 | 5
384 | 2026-02-14 17:59 | 87.2298 | 5808.0397 | Phase3_StableRated | 91.2829 | 7.946 | 64.7208 | 53.5492 | 56.3712 | 48.8349 | 135.4273 | 25.3871 | 28.5822 | 419.2451 | 45.9009 | 8.3811 | 31.9628 | 0.87179 | 7.0134 | 7.8174 | 9.2452 | 127 | 7 | 22 | 5
385 | 2026-02-14 17:59 | 87.457 | 5965.5501 | Phase3_StableRated | 92.4885 | 8.0455 | 65.175 | 53.8724 | 56.37 | 49.0435 | 136.4457 | 25.4015 | 28.5009 | 418.9316 | 45.9421 | 8.4408 | 32.0478 | 0.86283 | 7.9632 | 7.7213 | 9.3322 | 127 | 7 | 22 | 5
386 | 2026-02-14 18:00 | 87.6841 | 6010.8765 | Phase3_StableRated | 91.5978 | 8.0006 | 65.5206 | 53.5524 | 56.801 | 49.0041 | 135.7796 | 25.5977 | 28.5379 | 417.4473 | 45.9065 | 8.3748 | 32.0464 | 0.87394 | 6.1854 | 7.6963 | 12.4974 | 127 | 7 | 22 | 5
387 | 2026-02-14 18:00 | 87.9113 | 6266.0003 | Phase3_StableRated | 91.8988 | 8.0251 | 64.5057 | 53.5353 | 56.4112 | 49.052 | 136.7228 | 25.5426 | 28.7205 | 418.2424 | 45.695 | 8.3326 | 31.9929 | 0.87148 | 6.7667 | 7.5378 | 10.6902 | 127 | 7 | 22 | 5
388 | 2026-02-14 18:00 | 88.1385 | 6136.8239 | Phase3_StableRated | 93.327 | 8.0736 | 64.2663 | 53.9107 | 56.9566 | 48.9684 | 135.6555 | 25.4729 | 28.5689 | 417.7715 | 45.6465 | 8.3624 | 31.9135 | 0.86846 | 7.1389 | 7.5651 | 13.9901 | 127 | 7 | 22 | 5
389 | 2026-02-14 18:00 | 88.3656 | 5913.6751 | Phase3_StableRated | 92.0491 | 8.0589 | 65.4596 | 53.6691 | 56.3221 | 48.9914 | 136.0036 | 25.3808 | 28.6611 | 420.7956 | 45.4003 | 8.395 | 32.0157 | 0.86697 | 8.025 | 7.6985 | 12.7391 | 127 | 7 | 22 | 5
390 | 2026-02-14 18:00 | 88.5928 | 5878.886 | Phase3_StableRated | 92.181 | 8.0671 | 64.8835 | 53.5955 | 56.7115 | 49.3612 | 136.9136 | 25.5132 | 28.4764 | 420.8792 | 45.4126 | 8.3912 | 31.9955 | 0.87514 | 6.9976 | 8.1881 | 8.4654 | 127 | 7 | 22 | 5
391 | 2026-02-14 18:01 | 88.8199 | 6111.503 | Phase3_StableRated | 92.3331 | 8.0135 | 64.7914 | 53.8824 | 56.2005 | 49.1939 | 136.3302 | 25.3717 | 28.6995 | 419.5044 | 46.1781 | 8.299 | 32.0144 | 0.86464 | 7.4178 | 7.7401 | 5.1754 | 127 | 7 | 22 | 5
392 | 2026-02-14 18:01 | 89.0471 | 5843.8619 | Phase3_StableRated | 92.3977 | 8.0143 | 64.9976 | 54.125 | 56.6072 | 49.05 | 136.067 | 25.4793 | 28.6589 | 419.9012 | 46.1067 | 8.3623 | 32.0032 | 0.85984 | 6.7912 | 7.5468 | 13.4015 | 127 | 7 | 22 | 5
393 | 2026-02-14 18:01 | 89.2743 | 6351.6194 | Phase3_StableRated | 92.2564 | 8.0118 | 64.2231 | 53.7142 | 57.0936 | 48.9986 | 135.3845 | 25.5492 | 28.613 | 419.1072 | 45.8483 | 8.2795 | 31.9746 | 0.87254 | 7.3177 | 7.5262 | 13.0416 | 127 | 7 | 22 | 5
394 | 2026-02-14 18:02 | 89.5014 | 6265.2019 | Phase3_StableRated | 92.3555 | 7.9523 | 65.0063 | 53.6931 | 56.7017 | 49.0734 | 135.4352 | 25.3717 | 28.749 | 419.2565 | 46.0941 | 8.4127 | 31.9711 | 0.86995 | 8.1611 | 7.6095 | 5.9158 | 127 | 7 | 22 | 5
395 | 2026-02-14 18:02 | 89.7286 | 6023.1067 | Phase3_StableRated | 93.0869 | 7.971 | 64.8075 | 53.6229 | 56.4206 | 49.1109 | 135.3165 | 25.2788 | 28.7228 | 417.9331 | 45.7377 | 8.3899 | 31.966 | 0.86495 | 7.7617 | 8.1344 | 13.5632 | 127 | 7 | 22 | 5
396 | 2026-02-14 18:02 | 89.9558 | 5844.2227 | Phase3_StableRated | 92.2855 | 7.9964 | 65.1008 | 53.5723 | 56.5672 | 49.003 | 135.594 | 25.7366 | 28.6096 | 419.44 | 45.7774 | 8.3482 | 31.9192 | 0.8602 | 7.0686 | 7.6101 | 10.6452 | 127 | 7 | 22 | 5
397 | 2026-02-14 18:02 | 90.1829 | 6338.7516 | Phase3_StableRated | 92.3296 | 8.0248 | 64.6452 | 53.5811 | 56.6614 | 48.9226 | 136.307 | 25.4049 | 28.4589 | 418.7413 | 45.7747 | 8.4057 | 31.9139 | 0.86744 | 7.276 | 7.8821 | 10.0409 | 127 | 7 | 22 | 5
398 | 2026-02-14 18:02 | 90.4101 | 6124.8059 | Phase3_StableRated | 92.6222 | 8.0334 | 64.9938 | 53.2936 | 56.8904 | 48.9934 | 135.8289 | 25.6403 | 28.9081 | 420.2499 | 45.8644 | 8.3697 | 31.9289 | 0.86286 | 7.4774 | 7.6064 | 13.9324 | 127 | 7 | 22 | 5
399 | 2026-02-14 18:03 | 90.6372 | 6351.4904 | Phase3_StableRated | 92.6682 | 7.9631 | 64.7869 | 53.7007 | 56.6191 | 48.5441 | 134.9315 | 25.5082 | 28.6014 | 419.4833 | 45.7762 | 8.308 | 31.9497 | 0.86827 | 7.4656 | 7.7382 | 13.2407 | 127 | 7 | 22 | 5
400 | 2026-02-14 18:03 | 90.8644 | 5924.5015 | Phase3_StableRated | 92.467 | 8.0193 | 65.1435 | 53.4305 | 56.7935 | 49.0759 | 137.5696 | 25.4875 | 28.7743 | 419.5813 | 45.9398 | 8.3805 | 31.9735 | 0.85861 | 7.8914 | 7.8726 | 11.1632 | 127 | 7 | 22 | 5
401 | 2026-02-14 18:03 | 91.0916 | 6095.3718 | Phase3_StableRated | 92.5201 | 8.0038 | 64.9246 | 53.9996 | 56.025 | 48.9302 | 136.1695 | 25.4898 | 28.8739 | 419.3676 | 45.7008 | 8.3316 | 31.9059 | 0.86846 | 7.7353 | 7.5923 | 10.7287 | 127 | 7 | 22 | 5
402 | 2026-02-14 18:04 | 91.3187 | 6205.2528 | Phase3_StableRated | 91.4943 | 8.0744 | 64.9682 | 53.8068 | 56.6343 | 49.4307 | 134.8711 | 25.4712 | 29.2021 | 419.4863 | 45.8765 | 8.309 | 32.0467 | 0.862 | 7.0385 | 7.5707 | 11.2031 | 127 | 7 | 22 | 5
403 | 2026-02-14 18:04 | 91.5459 | 6227.2064 | Phase3_StableRated | 92.8227 | 7.9942 | 64.7977 | 53.8164 | 56.6695 | 49.0231 | 135.7744 | 25.501 | 28.5388 | 419.1205 | 45.8579 | 8.3765 | 31.8388 | 0.8707 | 7.6219 | 8.0271 | 8.8071 | 127 | 7 | 22 | 5
404 | 2026-02-14 18:04 | 91.773 | 6164.9971 | Phase3_StableRated | 91.8424 | 8.0476 | 65.1334 | 53.7061 | 57.0527 | 48.8261 | 136.3665 | 25.449 | 28.7734 | 419.5355 | 45.8675 | 8.338 | 32.0429 | 0.87056 | 7.0509 | 7.8857 | 9.7426 | 127 | 7 | 22 | 5
405 | 2026-02-14 18:04 | 92.0002 | 6348.0304 | Phase3_StableRated | 92.534 | 8.0159 | 65.3147 | 53.6656 | 56.7672 | 48.9127 | 137.6641 | 25.3468 | 28.6503 | 418.4509 | 45.5887 | 8.4006 | 32.0298 | 0.86167 | 6.6697 | 7.8557 | 7.4676 | 127 | 7 | 22 | 5
406 | 2026-02-14 18:05 | 92.2274 | 6099.3971 | Phase3_StableRated | 91.8624 | 8.0453 | 65.0985 | 54.1418 | 56.5949 | 48.8913 | 135.081 | 25.5467 | 28.6441 | 419.6977 | 45.3941 | 8.3799 | 31.9341 | 0.87233 | 6.9142 | 7.8612 | 8.8609 | 127 | 7 | 22 | 5
407 | 2026-02-14 18:05 | 92.4545 | 6259.3623 | Phase3_StableRated | 92.111 | 8.045 | 65.0876 | 53.3833 | 56.6635 | 49.0741 | 136.6577 | 25.4888 | 28.5578 | 419.3753 | 45.8829 | 8.4283 | 31.8668 | 0.87157 | 6.9131 | 7.7872 | 8.8731 | 127 | 7 | 22 | 5
408 | 2026-02-14 18:05 | 92.6817 | 6315.8285 | Phase3_StableRated | 92.1339 | 8.0492 | 64.7731 | 54.1343 | 56.9101 | 49.1017 | 137.4237 | 25.4499 | 28.5622 | 419.5125 | 45.6824 | 8.3723 | 31.9179 | 0.87108 | 6.1957 | 8.0995 | 8.2899 | 127 | 7 | 22 | 5
409 | 2026-02-14 18:05 | 92.9088 | 6392.8312 | Phase3_StableRated | 92.3145 | 8.051 | 65.262 | 53.8154 | 56.8266 | 49.2661 | 135.3769 | 25.3047 | 28.7059 | 419.5264 | 45.627 | 8.3919 | 31.8308 | 0.86061 | 7.5744 | 7.7155 | 10.0209 | 127 | 7 | 22 | 5
410 | 2026-02-14 18:06 | 93.136 | 6439.0659 | Phase3_StableRated | 92.4413 | 7.9808 | 64.8458 | 53.7008 | 56.8141 | 48.9069 | 135.6942 | 25.655 | 28.4423 | 419.8976 | 45.8671 | 8.3684 | 32.0161 | 0.88225 | 5.2095 | 7.8041 | 9.1155 | 127 | 7 | 22 | 5
411 | 2026-02-14 18:06 | 93.3632 | 6167.6594 | Phase3_StableRated | 92.977 | 8.0464 | 65.7657 | 53.7309 | 56.6449 | 49.0891 | 135.2793 | 25.5941 | 28.737 | 419.9506 | 46.1876 | 8.3421 | 31.806 | 0.86856 | 8.9852 | 7.3712 | 11.456 | 127 | 7 | 22 | 5
412 | 2026-02-14 18:06 | 93.5903 | 6119.13 | Phase3_StableRated | 92.3846 | 8.0562 | 64.8549 | 54.2461 | 57.1211 | 48.877 | 135.8269 | 25.6126 | 28.716 | 419.7473 | 45.4841 | 8.4214 | 31.9317 | 0.86363 | 8.0716 | 7.5332 | 5.6156 | 127 | 7 | 22 | 5
413 | 2026-02-14 18:06 | 93.8175 | 6573.7918 | Phase3_StableRated | 92.056 | 8.0642 | 65.8309 | 53.5912 | 56.7152 | 49.216 | 135.9626 | 25.4331 | 28.7615 | 420.0246 | 45.3679 | 8.3781 | 31.8335 | 0.86492 | 6.9096 | 7.4563 | 9.4876 | 127 | 7 | 22 | 5
414 | 2026-02-14 18:06 | 94.0447 | 6441.5512 | Phase3_StableRated | 92.4862 | 8.0952 | 65.2373 | 53.5483 | 56.8277 | 49.3747 | 136.6841 | 25.326 | 28.6541 | 419.4912 | 45.8242 | 8.3157 | 31.9493 | 0.86341 | 7.1982 | 7.9589 | 10.1891 | 127 | 7 | 22 | 5
415 | 2026-02-14 18:07 | 94.2718 | 6288.154 | Phase3_StableRated | 92.9 | 8.0598 | 65.1698 | 54.063 | 57.3107 | 49.0993 | 137.1011 | 25.653 | 28.6835 | 420.598 | 45.6867 | 8.3695 | 31.8719 | 0.86577 | 7.436 | 7.176 | 9.0502 | 127 | 7 | 22 | 5
416 | 2026-02-14 18:07 | 94.499 | 6662.8129 | Phase3_StableRated | 91.6705 | 7.9588 | 65.6975 | 53.9523 | 56.457 | 49.1931 | 135.1857 | 25.4656 | 28.7843 | 418.7598 | 45.7161 | 8.4104 | 31.8503 | 0.85493 | 6.5503 | 7.6425 | 9.0979 | 127 | 7 | 22 | 5
417 | 2026-02-14 18:07 | 94.7261 | 6454.0119 | Phase3_StableRated | 92.4057 | 8.0515 | 65.3632 | 53.6418 | 56.491 | 49.288 | 134.3843 | 25.3939 | 28.6283 | 420.3898 | 45.8625 | 8.4132 | 31.9654 | 0.86294 | 7.2341 | 7.1086 | 5.531 | 127 | 7 | 22 | 5
418 | 2026-02-14 18:08 | 94.9533 | 6635.5935 | Phase3_StableRated | 92.4212 | 8.0339 | 65.0196 | 54.0467 | 56.8826 | 49.3968 | 135.8094 | 25.5754 | 28.6202 | 420.2728 | 45.9852 | 8.4102 | 31.8871 | 0.86585 | 6.8556 | 7.5339 | 10.7369 | 127 | 7 | 22 | 5
419 | 2026-02-14 18:08 | 95.1805 | 6477.3573 | Phase3_StableRated | 92.3249 | 8.07 | 65.0608 | 53.6958 | 56.663 | 49.1126 | 136.2033 | 25.6675 | 28.636 | 420.9118 | 45.5268 | 8.3825 | 31.9126 | 0.8547 | 6.9921 | 7.6184 | 11.3127 | 127 | 7 | 22 | 5
420 | 2026-02-14 18:08 | 95.4076 | 6804.1522 | Phase3_StableRated | 93.0491 | 8.0543 | 65.4996 | 54.0746 | 56.7125 | 49.2323 | 136.5645 | 25.4402 | 28.6825 | 420.4391 | 45.5323 | 8.3354 | 31.8342 | 0.85431 | 7.4862 | 7.9948 | 11.0357 | 127 | 7 | 22 | 5
421 | 2026-02-14 18:08 | 95.6348 | 6771.8786 | Phase3_StableRated | 91.7375 | 7.9595 | 65.3147 | 54.1285 | 56.745 | 48.9466 | 135.7516 | 25.6434 | 28.5176 | 420.5044 | 45.8029 | 8.4576 | 31.794 | 0.8636 | 6.2423 | 7.8097 | 12.2264 | 127 | 7 | 22 | 5
422 | 2026-02-14 18:09 | 95.8619 | 6474.2215 | Phase3_StableRated | 92.2144 | 8.0912 | 64.896 | 54.2201 | 56.8974 | 49.0407 | 136.1512 | 25.723 | 28.8504 | 419.2625 | 45.7815 | 8.363 | 31.8862 | 0.86504 | 7.1496 | 7.5261 | 10.491 | 127 | 7 | 22 | 5
423 | 2026-02-14 18:09 | 96.0891 | 6680.3143 | Phase3_StableRated | 91.9214 | 7.9772 | 65.1037 | 53.8846 | 57.1409 | 49.039 | 136.9245 | 25.3573 | 28.6583 | 420.5169 | 46.0924 | 8.432 | 31.8741 | 0.86341 | 6.9259 | 7.9566 | 10.701 | 127 | 7 | 22 | 5
424 | 2026-02-14 18:09 | 96.3163 | 6644.7936 | Phase3_StableRated | 92.0371 | 8.0623 | 65.1497 | 54.3951 | 57.3052 | 49.3088 | 136.5597 | 25.3614 | 28.9 | 419.7942 | 45.8287 | 8.3105 | 31.9018 | 0.85706 | 7.361 | 7.71 | 10.2849 | 127 | 7 | 22 | 5
425 | 2026-02-14 18:09 | 96.5434 | 6773.2067 | Phase3_StableRated | 91.4919 | 8.0476 | 65.0647 | 54.0523 | 56.9478 | 49.137 | 135.4371 | 25.6232 | 28.8479 | 420.4629 | 45.779 | 8.3882 | 31.8134 | 0.87386 | 6.7472 | 7.7316 | 11.4405 | 127 | 7 | 22 | 5
426 | 2026-02-14 18:10 | 96.7706 | 6424.1177 | Phase3_StableRated | 91.4234 | 7.995 | 65.1833 | 53.8723 | 56.6116 | 49.1948 | 136.0255 | 25.2865 | 28.5049 | 421.1821 | 45.5916 | 8.3539 | 31.756 | 0.8617 | 8.1839 | 7.4302 | 6.2484 | 127 | 7 | 22 | 5
427 | 2026-02-14 18:10 | 96.9977 | 6697.4492 | Phase3_StableRated | 92.9771 | 8.0375 | 65.6637 | 54.0678 | 56.6096 | 49.2183 | 135.8437 | 25.4946 | 28.5775 | 419.2203 | 45.6476 | 8.3222 | 31.8474 | 0.8649 | 6.8422 | 7.5119 | 7.5363 | 127 | 7 | 22 | 5
428 | 2026-02-14 18:10 | 97.2249 | 6771.0512 | Phase3_StableRated | 91.533 | 8.0262 | 65.0114 | 54.2024 | 56.3631 | 49.0589 | 137.4375 | 25.3302 | 29.1313 | 419.6941 | 45.669 | 8.3403 | 31.8098 | 0.86383 | 7.292 | 7.5618 | 13.6953 | 127 | 7 | 22 | 5
429 | 2026-02-14 18:10 | 97.4521 | 6346.418 | Phase3_StableRated | 91.4892 | 8.0269 | 65.2722 | 53.8024 | 56.7917 | 49.3649 | 136.0006 | 25.4617 | 28.9483 | 420.7724 | 45.8013 | 8.4013 | 31.884 | 0.85835 | 8.0602 | 7.7163 | 3.6576 | 127 | 7 | 22 | 5
430 | 2026-02-14 18:10 | 97.6792 | 6451.7473 | Phase3_StableRated | 90.7389 | 8.0282 | 65.6524 | 53.7689 | 57.1153 | 48.8665 | 135.9573 | 25.5028 | 28.7262 | 419.9151 | 45.6982 | 8.3424 | 31.7653 | 0.8687 | 7.014 | 7.7361 | 9.4407 | 127 | 7 | 22 | 5
431 | 2026-02-14 18:11 | 97.9064 | 6333.4702 | Phase3_StableRated | 91.8225 | 8.0516 | 65.4347 | 54.2096 | 56.9008 | 49.2119 | 135.4567 | 25.4956 | 28.7566 | 421.2641 | 45.4294 | 8.4165 | 31.8515 | 0.86469 | 7.117 | 8.0418 | 12.749 | 127 | 7 | 22 | 5
432 | 2026-02-14 18:11 | 98.1336 | 6625.3673 | Phase3_StableRated | 91.5209 | 8.1006 | 64.8726 | 54.1077 | 56.8566 | 49.1853 | 136.9764 | 25.4636 | 28.7138 | 419.641 | 45.7694 | 8.3928 | 31.7987 | 0.85936 | 7.0695 | 7.8128 | 9.418 | 127 | 7 | 22 | 5
433 | 2026-02-14 18:11 | 98.3607 | 6794.9718 | Phase3_StableRated | 93.1535 | 8.0633 | 64.9725 | 53.8308 | 56.9763 | 49.3665 | 137.5429 | 25.4677 | 28.8006 | 419.5075 | 45.8885 | 8.4035 | 31.7551 | 0.85823 | 7.8261 | 7.1741 | 8.6916 | 127 | 7 | 22 | 5
434 | 2026-02-14 18:11 | 98.5879 | 6933.0011 | Phase3_StableRated | 92.842 | 8.0105 | 65.5763 | 54.2612 | 56.7698 | 49.0765 | 136.1678 | 25.7615 | 28.5524 | 421.1565 | 46.0154 | 8.4058 | 31.8353 | 0.87065 | 6.7531 | 7.7644 | 10.3068 | 127 | 7 | 22 | 5
435 | 2026-02-14 18:12 | 98.815 | 6725.3272 | Phase3_StableRated | 91.8267 | 8.0333 | 65.5706 | 54.6516 | 56.9916 | 49.3397 | 136.0206 | 25.7616 | 28.3536 | 421.2385 | 45.9242 | 8.4562 | 31.7016 | 0.86101 | 7.892 | 7.3979 | 9.2776 | 127 | 7 | 22 | 5
436 | 2026-02-14 18:12 | 99.0422 | 6983.5917 | Phase3_StableRated | 93.2816 | 7.9741 | 65.2261 | 53.9604 | 56.8916 | 49.3077 | 136.1619 | 25.3954 | 28.5652 | 419.0066 | 45.8356 | 8.4036 | 31.8266 | 0.86199 | 7.1221 | 7.519 | 10.0029 | 127 | 7 | 22 | 5
437 | 2026-02-14 18:12 | 99.2694 | 6529.0361 | Phase3_StableRated | 93.0017 | 8.022 | 64.7983 | 53.9082 | 56.6451 | 49.3571 | 134.0473 | 25.7149 | 28.7178 | 420.3932 | 46.1168 | 8.3508 | 31.7252 | 0.86322 | 6.551 | 7.5503 | 8.192 | 127 | 7 | 22 | 5
438 | 2026-02-14 18:12 | 99.4965 | 6493.9705 | Phase3_StableRated | 91.8621 | 8.115 | 65.6396 | 53.8314 | 57.141 | 49.1603 | 136.8137 | 25.4897 | 28.5662 | 420.8216 | 45.7498 | 8.4137 | 31.7082 | 0.85203 | 7.6844 | 7.5727 | 12.8921 | 127 | 7 | 22 | 5
439 | 2026-02-14 18:13 | 99.7237 | 6766.8115 | Phase3_StableRated | 90.6649 | 8.0842 | 65.1622 | 54.2731 | 57.0834 | 49.425 | 136.1663 | 25.5792 | 28.8103 | 419.1996 | 45.7113 | 8.3141 | 31.7153 | 0.86548 | 6.9294 | 7.4624 | 13.2659 | 127 | 7 | 22 | 5
440 | 2026-02-14 18:13 | 99.9508 | 6850.9171 | Phase3_StableRated | 93.2924 | 8.0458 | 64.8729 | 54.422 | 56.8286 | 49.1554 | 136.3949 | 25.5003 | 28.6655 | 418.8614 | 45.6012 | 8.3902 | 31.781 | 0.8508 | 7.5244 | 7.7841 | 9.3222 | 127 | 7 | 22 | 5
441 | 2026-02-14 18:13 | 100.178 | 6801.2492 | Phase3_StableRated | 91.4754 | 8.0486 | 64.9107 | 54.3574 | 57.1615 | 49.2668 | 135.2276 | 25.451 | 28.6551 | 419.4298 | 45.8841 | 8.3786 | 31.7542 | 0.86614 | 5.152 | 7.453 | 6.1329 | 127 | 7 | 22 | 5
442 | 2026-02-14 18:14 | 100.4052 | 6498.8366 | Phase3_StableRated | 91.5157 | 8.0428 | 65.4254 | 54.1571 | 57.5264 | 49.3098 | 135.7369 | 25.6508 | 28.9032 | 420.3294 | 45.2159 | 8.4205 | 31.7162 | 0.86722 | 7.1355 | 7.8119 | 8.3976 | 127 | 7 | 22 | 5
443 | 2026-02-14 18:14 | 100.6323 | 6823.3028 | Phase3_StableRated | 92.6296 | 8.0676 | 64.9836 | 54.1646 | 57.0476 | 49.5392 | 135.8136 | 25.5072 | 28.8515 | 421.2445 | 45.6563 | 8.3951 | 31.7516 | 0.84879 | 6.9078 | 8.1998 | 9.252 | 127 | 7 | 22 | 5
444 | 2026-02-14 18:14 | 100.8595 | 6648.8879 | Phase3_StableRated | 93.1946 | 8.0586 | 64.626 | 53.8744 | 57.1978 | 49.341 | 136.9793 | 25.4203 | 28.7498 | 420.429 | 45.7723 | 8.3455 | 31.6174 | 0.85591 | 6.4868 | 7.453 | 11.2239 | 127 | 7 | 22 | 5
445 | 2026-02-14 18:14 | 101.0866 | 6972.7011 | Phase3_StableRated | 92.9987 | 8.0254 | 65.5155 | 54.4434 | 56.8737 | 49.0647 | 135.47 | 25.4023 | 28.838 | 419.5953 | 45.5974 | 8.3437 | 31.7113 | 0.87174 | 6.5549 | 7.6794 | 7.2145 | 127 | 7 | 22 | 5
446 | 2026-02-14 18:14 | 101.3138 | 6940.792 | Phase3_StableRated | 92.3932 | 8.0464 | 65.6173 | 54.3653 | 57.0972 | 49.3179 | 137.7027 | 25.4161 | 28.7279 | 420.2447 | 45.7301 | 8.3755 | 31.7631 | 0.8572 | 6.6813 | 7.1958 | 8.1455 | 127 | 7 | 22 | 5
447 | 2026-02-14 18:15 | 101.541 | 6752.1419 | Phase3_StableRated | 92.3157 | 8.0762 | 65.5311 | 53.7799 | 57.2041 | 49.592 | 136.2338 | 25.3738 | 28.9726 | 417.884 | 45.9082 | 8.3624 | 31.6303 | 0.85711 | 6.9557 | 7.6882 | 10.9764 | 127 | 7 | 22 | 5
448 | 2026-02-14 18:15 | 101.7681 | 6834.123 | Phase3_StableRated | 92.4738 | 8.0329 | 65.1031 | 54.5277 | 57.0933 | 49.0082 | 134.9351 | 25.5688 | 28.7633 | 419.6821 | 45.8223 | 8.3221 | 31.8023 | 0.86055 | 6.1882 | 7.8856 | 12.0359 | 127 | 7 | 22 | 5
449 | 2026-02-14 18:15 | 101.9953 | 6764.3687 | Phase3_StableRated | 92.5801 | 8.0802 | 65.2481 | 54.2159 | 56.6912 | 49.4986 | 135.9516 | 25.4098 | 28.6382 | 418.7815 | 45.6827 | 8.375 | 31.717 | 0.85825 | 7.3408 | 7.8652 | 8.5133 | 127 | 7 | 22 | 5
450 | 2026-02-14 18:16 | 102.2224 | 6935.4706 | Phase3_StableRated | 92.0459 | 8.0466 | 65.559 | 54.4458 | 57.124 | 49.4563 | 135.3877 | 25.5136 | 28.5513 | 419.8388 | 45.869 | 8.3766 | 31.7283 | 0.86838 | 7.9309 | 7.7481 | 6.5231 | 127 | 7 | 22 | 5
451 | 2026-02-14 18:16 | 102.4496 | 7109.8976 | Phase3_StableRated | 92.4392 | 8.0118 | 65.6038 | 53.9196 | 57.2512 | 49.4851 | 134.3511 | 25.7705 | 28.6514 | 420.8257 | 45.8417 | 8.3749 | 31.7577 | 0.8666 | 7.4152 | 7.8976 | 18.5591 | 127 | 7 | 22 | 5
452 | 2026-02-14 18:16 | 102.6768 | 6822.1499 | Phase3_StableRated | 92.1049 | 8.0508 | 65.7045 | 54.1236 | 57.1096 | 49.2682 | 137.1706 | 25.7415 | 28.9041 | 418.7313 | 45.9738 | 8.3619 | 31.6268 | 0.8613 | 7.4892 | 8.2757 | 11.6983 | 127 | 7 | 22 | 5
453 | 2026-02-14 18:16 | 102.9039 | 7070.3001 | Phase3_StableRated | 91.7765 | 7.9857 | 65.1829 | 54.1766 | 57.3392 | 48.8796 | 136.5103 | 25.5656 | 28.9003 | 420.4563 | 45.8271 | 8.3391 | 31.5853 | 0.87259 | 7.7458 | 8.088 | 9.2348 | 127 | 7 | 22 | 5
454 | 2026-02-14 18:16 | 103.1311 | 6924.1661 | Phase3_StableRated | 92.1723 | 7.9949 | 65.4592 | 54.2727 | 57.1295 | 49.2676 | 136.3797 | 25.4876 | 28.9382 | 420.2531 | 45.5405 | 8.4315 | 31.7695 | 0.85872 | 7.8479 | 7.6512 | 11.8868 | 127 | 7 | 22 | 5
455 | 2026-02-14 18:17 | 103.3583 | 6898.5771 | Phase3_StableRated | 91.1667 | 8.0404 | 65.5102 | 54.5196 | 57.3346 | 49.4831 | 136.2509 | 25.8037 | 28.4472 | 419.995 | 46.1047 | 8.387 | 31.6706 | 0.86099 | 8.4053 | 7.4172 | 9.9036 | 127 | 7 | 22 | 5
456 | 2026-02-14 18:17 | 103.5854 | 7021.146 | Phase3_StableRated | 92.117 | 8.0633 | 65.6632 | 54.4133 | 57.1444 | 49.0447 | 135.0483 | 25.602 | 29.0237 | 419.2203 | 45.8551 | 8.4505 | 31.5681 | 0.85897 | 6.9175 | 7.6796 | 11.8542 | 127 | 7 | 22 | 5
457 | 2026-02-14 18:17 | 103.8126 | 6891.5845 | Phase3_StableRated | 91.6302 | 8.0188 | 65.4951 | 54.2655 | 56.8499 | 49.2015 | 135.5682 | 25.5723 | 28.5786 | 419.7493 | 45.7999 | 8.35 | 31.5484 | 0.85514 | 6.5922 | 7.5655 | 10.0979 | 127 | 7 | 22 | 5
458 | 2026-02-14 18:18 | 104.0397 | 6982.2478 | Phase3_StableRated | 91.6538 | 8.0361 | 65.5759 | 54.1758 | 57.1451 | 49.928 | 136.5418 | 25.3296 | 28.8448 | 420.3933 | 45.7329 | 8.3967 | 31.7555 | 0.86762 | 7.4754 | 7.8363 | 10.1367 | 127 | 7 | 22 | 5
459 | 2026-02-14 18:18 | 104.2669 | 6897.0472 | Phase3_StableRated | 92.6152 | 8.0127 | 65.5354 | 54.5537 | 56.9003 | 49.4394 | 134.6272 | 25.5439 | 28.6531 | 421.016 | 45.8434 | 8.3977 | 31.6601 | 0.859 | 7.1628 | 7.5138 | 9.4728 | 127 | 7 | 22 | 5
460 | 2026-02-14 18:18 | 104.4941 | 7406.5091 | Phase3_StableRated | 92.7134 | 8.07 | 65.8689 | 54.1608 | 57.0725 | 49.4672 | 134.0567 | 25.6409 | 28.7796 | 419.1916 | 45.7594 | 8.3649 | 31.6702 | 0.87009 | 7.7309 | 7.7014 | 6.5722 | 127 | 7 | 22 | 5
461 | 2026-02-14 18:18 | 104.7212 | 7120.5432 | Phase3_StableRated | 92.6194 | 8.0386 | 65.5518 | 54.4303 | 57.1929 | 49.2789 | 135.4158 | 25.4444 | 28.5854 | 419.8865 | 45.9638 | 8.378 | 31.7325 | 0.85904 | 8.0178 | 7.9388 | 14.6131 | 127 | 7 | 22 | 5
462 | 2026-02-14 18:18 | 104.9484 | 7021.165 | Phase3_StableRated | 91.6505 | 8.0195 | 65.3591 | 54.2771 | 57.2469 | 49.1312 | 135.7982 | 25.5539 | 28.8982 | 419.1998 | 45.729 | 8.3896 | 31.7079 | 0.86803 | 7.0281 | 7.7259 | 7.5173 | 127 | 7 | 22 | 5
463 | 2026-02-14 18:19 | 105.1755 | 7179.3282 | Phase3_StableRated | 91.4993 | 8.0555 | 65.8122 | 54.568 | 56.899 | 49.4813 | 136.0475 | 25.5006 | 28.5337 | 420.2486 | 45.7499 | 8.3932 | 31.7781 | 0.8617 | 7.3146 | 7.5469 | 6.5309 | 127 | 7 | 22 | 5
464 | 2026-02-14 18:19 | 105.4027 | 7143.7897 | Phase3_StableRated | 92.8794 | 7.9625 | 65.5836 | 54.4464 | 57.3817 | 49.3962 | 136.6483 | 25.4823 | 28.634 | 419.858 | 45.8749 | 8.4274 | 31.6554 | 0.85783 | 6.4738 | 7.9755 | 9.5574 | 127 | 7 | 22 | 5
465 | 2026-02-14 18:19 | 105.6299 | 7142.2528 | Phase3_StableRated | 91.6469 | 7.9877 | 65.4303 | 53.9554 | 57.1871 | 49.2727 | 136.2841 | 25.2326 | 28.6062 | 417.7571 | 45.8973 | 8.3732 | 31.6616 | 0.86198 | 8.2948 | 7.37 | 7.3996 | 127 | 7 | 22 | 5
466 | 2026-02-14 18:20 | 105.857 | 7288.1428 | Phase3_StableRated | 92.1818 | 8.0369 | 65.5232 | 54.2816 | 57.0586 | 49.5118 | 135.8795 | 25.4846 | 28.4998 | 419.0134 | 45.9632 | 8.3766 | 31.6071 | 0.85747 | 6.6007 | 7.6915 | 9.6968 | 127 | 7 | 22 | 5
467 | 2026-02-14 18:20 | 106.0842 | 7325.9679 | Phase3_StableRated | 92.5134 | 8.0514 | 65.6505 | 54.2038 | 56.76 | 49.6091 | 136.8448 | 25.539 | 28.7222 | 417.956 | 45.7804 | 8.4076 | 31.5716 | 0.86757 | 6.7632 | 7.7355 | 11.7855 | 127 | 7 | 22 | 5
468 | 2026-02-14 18:20 | 106.3113 | 7140.2029 | Phase3_StableRated | 91.6846 | 8.0326 | 65.5947 | 54.4818 | 57.1188 | 49.5899 | 134.8437 | 25.4063 | 29.0343 | 418.9317 | 45.8858 | 8.3047 | 31.6216 | 0.86222 | 6.9467 | 7.7565 | 12.4722 | 127 | 7 | 22 | 5
469 | 2026-02-14 18:20 | 106.5385 | 7148.5578 | Phase3_StableRated | 92.0599 | 8.1484 | 65.5859 | 54.2601 | 57.0073 | 49.3343 | 136.2269 | 25.5088 | 29.1531 | 419.0744 | 45.897 | 8.2924 | 31.5983 | 0.86862 | 6.5095 | 7.8095 | 11.7844 | 127 | 7 | 22 | 5
470 | 2026-02-14 18:20 | 106.7657 | 7210.9743 | Phase3_StableRated | 91.4202 | 8.0288 | 65.8888 | 54.3773 | 56.9549 | 49.5637 | 136.6432 | 25.4095 | 28.7405 | 419.3006 | 46.0149 | 8.3919 | 31.5466 | 0.87655 | 6.7017 | 7.8607 | 9.3937 | 127 | 7 | 22 | 5
471 | 2026-02-14 18:21 | 106.9928 | 6909.7923 | Phase3_StableRated | 91.9249 | 8.1003 | 65.8511 | 54.251 | 57.0584 | 49.1433 | 135.0782 | 25.5748 | 28.909 | 419.569 | 45.871 | 8.3886 | 31.6468 | 0.86317 | 6.8318 | 7.7385 | 10.1895 | 127 | 7 | 22 | 5
472 | 2026-02-14 18:21 | 107.22 | 7048.1208 | Phase3_StableRated | 92.2418 | 7.9856 | 65.8856 | 54.451 | 56.7704 | 49.2252 | 134.4117 | 25.5388 | 28.7366 | 419.3819 | 45.8081 | 8.3762 | 31.6866 | 0.8722 | 5.9261 | 7.6808 | 10.9891 | 127 | 7 | 22 | 5
473 | 2026-02-14 18:21 | 107.4472 | 7513.7601 | Phase3_StableRated | 91.1387 | 8.0485 | 65.3572 | 54.0777 | 56.9352 | 49.8464 | 135.0702 | 25.3907 | 28.8325 | 419.8446 | 46.1629 | 8.3477 | 31.6346 | 0.86877 | 6.3285 | 7.6878 | 5.2745 | 127 | 7 | 22 | 5
474 | 2026-02-14 18:22 | 107.6743 | 7572.6348 | Phase3_StableRated | 92.2105 | 7.9581 | 65.7526 | 54.4839 | 57.1667 | 49.656 | 135.2576 | 25.7073 | 28.5941 | 420.1121 | 45.303 | 8.4049 | 31.5762 | 0.87041 | 8.2178 | 7.6064 | 11.7385 | 127 | 7 | 22 | 5
475 | 2026-02-14 18:22 | 107.9015 | 7292.2077 | Phase3_StableRated | 92.3285 | 7.9928 | 65.2932 | 54.247 | 57.4624 | 49.6142 | 136.5454 | 25.6553 | 28.7693 | 418.5924 | 46.3106 | 8.3225 | 31.4995 | 0.87393 | 7.504 | 7.9154 | 6.2894 | 127 | 7 | 22 | 5
476 | 2026-02-14 18:22 | 108.1286 | 7436.607 | Phase3_StableRated | 92.6517 | 8.0095 | 65.7469 | 54.2028 | 57.045 | 49.304 | 135.4174 | 25.4166 | 28.8223 | 418.684 | 45.5989 | 8.3296 | 31.5561 | 0.8606 | 7.6409 | 7.6234 | 15.2252 | 127 | 7 | 22 | 5
477 | 2026-02-14 18:22 | 108.3558 | 7410.5975 | Phase3_StableRated | 92.1311 | 8.0026 | 66.1095 | 54.0966 | 57.7087 | 49.7178 | 135.2206 | 25.602 | 28.655 | 417.8682 | 45.6739 | 8.3704 | 31.6082 | 0.8568 | 7.8099 | 7.9243 | 9.0515 | 127 | 7 | 22 | 5
478 | 2026-02-14 18:22 | 108.583 | 7858.361 | Phase3_StableRated | 92.827 | 7.9513 | 65.6365 | 54.0224 | 56.9367 | 49.574 | 135.2385 | 25.5497 | 28.6919 | 418.1816 | 45.8216 | 8.4392 | 31.6085 | 0.86409 | 8.0946 | 7.758 | 9.5845 | 127 | 7 | 22 | 5
479 | 2026-02-14 18:23 | 108.8101 | 7567.7332 | Phase3_StableRated | 92.3686 | 8.0354 | 65.1157 | 54.1242 | 57.4284 | 49.4686 | 136.8001 | 25.5976 | 28.73 | 419.4738 | 45.8774 | 8.4137 | 31.6574 | 0.86463 | 5.8172 | 7.6507 | 8.0596 | 127 | 7 | 22 | 5
480 | 2026-02-14 18:23 | 109.0373 | 7388.2971 | Phase3_StableRated | 91.9354 | 7.997 | 65.4427 | 54.2883 | 57.0369 | 49.4581 | 135.5665 | 25.3975 | 28.8346 | 419.273 | 45.9095 | 8.4466 | 31.4994 | 0.85911 | 5.928 | 7.8994 | 8.2442 | 127 | 7 | 22 | 5
481 | 2026-02-14 18:23 | 109.2644 | 7274.4487 | Phase3_StableRated | 92.186 | 8.0202 | 65.4592 | 54.7182 | 57.2949 | 49.6199 | 135.9566 | 25.6395 | 28.6667 | 419.1542 | 45.5269 | 8.3843 | 31.5426 | 0.87002 | 6.642 | 7.6142 | 15.8027 | 127 | 7 | 22 | 5
482 | 2026-02-14 18:24 | 109.4916 | 7188.205 | Phase3_StableRated | 92.4856 | 8.0876 | 65.3961 | 54.313 | 57.2569 | 49.9679 | 135.716 | 25.4383 | 28.6528 | 420.3269 | 45.7948 | 8.3122 | 31.6369 | 0.86243 | 6.6264 | 7.873 | 12.6692 | 127 | 7 | 22 | 5
483 | 2026-02-14 18:24 | 109.7188 | 7486.3637 | Phase3_StableRated | 91.9667 | 8.0139 | 65.4078 | 54.3492 | 57.2627 | 49.6217 | 136.8365 | 25.4289 | 28.88 | 418.965 | 45.6484 | 8.3355 | 31.5433 | 0.86009 | 6.6984 | 7.7815 | 6.3681 | 127 | 7 | 22 | 5
484 | 2026-02-14 18:24 | 109.9459 | 7351.8657 | Phase3_StableRated | 92.0238 | 7.903 | 65.0533 | 54.4481 | 57.174 | 49.7423 | 135.1198 | 25.8066 | 28.8866 | 418.9217 | 45.906 | 8.3201 | 31.4823 | 0.8633 | 6.592 | 7.6443 | 13.8357 | 127 | 7 | 22 | 5
485 | 2026-02-14 18:24 | 110.1731 | 7263.2794 | Phase3_StableRated | 91.8518 | 8.0145 | 65.4905 | 54.3812 | 57.0468 | 49.3314 | 136.7385 | 25.4933 | 28.9037 | 419.1934 | 45.9105 | 8.4496 | 31.5151 | 0.86049 | 6.9478 | 7.8795 | 12.9973 | 127 | 7 | 22 | 5
486 | 2026-02-14 18:25 | 110.4002 | 7399.8819 | Phase3_StableRated | 91.7856 | 8.0326 | 65.923 | 54.5243 | 57.3082 | 49.8403 | 136.2894 | 25.5214 | 28.7093 | 419.9669 | 45.8027 | 8.3448 | 31.5203 | 0.85944 | 7.1997 | 7.8519 | 9.6299 | 127 | 7 | 22 | 5
487 | 2026-02-14 18:25 | 110.6274 | 7347.3686 | Phase3_StableRated | 91.4371 | 8.0835 | 65.3133 | 54.2276 | 57.0861 | 49.5587 | 135.7818 | 25.2334 | 28.7398 | 417.4524 | 45.6429 | 8.4192 | 31.4837 | 0.86963 | 6.5451 | 7.9866 | 11.0308 | 127 | 7 | 22 | 5
488 | 2026-02-14 18:25 | 110.8546 | 7795.2976 | Phase3_StableRated | 93.019 | 8.0109 | 66.0077 | 54.6863 | 57.3551 | 49.9387 | 138.1254 | 25.7191 | 28.9032 | 417.0628 | 45.7718 | 8.2976 | 31.6119 | 0.86261 | 5.686 | 7.9607 | 10.0552 | 127 | 7 | 22 | 5
489 | 2026-02-14 18:25 | 111.0817 | 7684.9046 | Phase3_StableRated | 91.2506 | 8.0007 | 65.9196 | 54.8471 | 57.5659 | 49.7134 | 134.9157 | 25.4194 | 29.0079 | 418.9294 | 45.8524 | 8.3308 | 31.4817 | 0.85942 | 6.2743 | 7.8856 | 14.8763 | 127 | 7 | 22 | 5
490 | 2026-02-14 18:26 | 111.3089 | 7561.3728 | Phase3_StableRated | 91.7918 | 8.0025 | 65.759 | 54.2315 | 56.8572 | 49.9441 | 135.6365 | 25.33 | 28.4344 | 417.2802 | 46.0021 | 8.4071 | 31.5585 | 0.86588 | 6.6717 | 7.5167 | 8.2688 | 127 | 7 | 22 | 5
491 | 2026-02-14 18:26 | 111.536 | 7809.2332 | Phase3_StableRated | 91.9069 | 8.0518 | 65.6225 | 54.24 | 57.3198 | 49.43 | 134.514 | 25.4302 | 28.613 | 418.4144 | 45.7742 | 8.3252 | 31.5716 | 0.85761 | 6.5642 | 8.2973 | 10.1032 | 127 | 7 | 22 | 5
492 | 2026-02-14 18:26 | 111.7632 | 7605.5717 | Phase3_StableRated | 92.627 | 8.1358 | 65.9785 | 54.4472 | 57.154 | 49.8208 | 136.4516 | 25.6067 | 28.9111 | 417.3337 | 45.7647 | 8.3403 | 31.5294 | 0.86269 | 6.0738 | 7.4899 | 8.8667 | 127 | 7 | 22 | 5
493 | 2026-02-14 18:26 | 111.9904 | 7474.3794 | Phase3_StableRated | 92.0372 | 7.9666 | 65.3777 | 54.1757 | 57.2136 | 49.6471 | 137.1327 | 25.5608 | 28.7156 | 417.4492 | 45.9996 | 8.3084 | 31.4738 | 0.86637 | 6.5456 | 7.9723 | 6.3103 | 127 | 7 | 22 | 5
494 | 2026-02-14 18:26 | 112.2175 | 7862.28 | Phase3_StableRated | 92.5865 | 8.0602 | 65.7368 | 54.486 | 57.1844 | 49.7273 | 137.0207 | 25.4436 | 28.6186 | 417.7295 | 45.902 | 8.3202 | 31.6119 | 0.87572 | 6.0486 | 7.8602 | 15.6711 | 127 | 7 | 22 | 5
495 | 2026-02-14 18:27 | 112.4447 | 7723.9705 | Phase3_StableRated | 91.6871 | 8.0482 | 65.7287 | 54.3167 | 56.8089 | 49.6706 | 136.6569 | 25.5194 | 28.5415 | 415.5007 | 46.0193 | 8.3326 | 31.5517 | 0.86065 | 6.7162 | 7.5309 | 7.0588 | 127 | 7 | 22 | 5
496 | 2026-02-14 18:27 | 112.6719 | 7493.1942 | Phase3_StableRated | 92.1492 | 8.0586 | 65.9444 | 54.9354 | 57.1365 | 49.6779 | 135.5877 | 25.459 | 28.7035 | 416.9255 | 45.8282 | 8.3062 | 31.5374 | 0.85875 | 6.1863 | 7.7587 | 10.5013 | 127 | 7 | 22 | 5
497 | 2026-02-14 18:27 | 112.899 | 7640.9229 | Phase3_StableRated | 91.5587 | 8.0125 | 65.1959 | 54.6646 | 57.5008 | 49.8243 | 135.4826 | 25.5455 | 28.4814 | 417.8542 | 45.5053 | 8.3448 | 31.4904 | 0.85366 | 6.3615 | 7.7375 | 5.8808 | 127 | 7 | 22 | 5
498 | 2026-02-14 18:27 | 113.1262 | 7549.3098 | Phase3_StableRated | 93.0893 | 8.0414 | 65.4791 | 54.6421 | 57.4619 | 49.8678 | 134.315 | 25.5777 | 28.9817 | 418.5696 | 46.0357 | 8.3708 | 31.3706 | 0.87221 | 5.9981 | 8.0378 | 9.1217 | 127 | 7 | 22 | 5
499 | 2026-02-14 18:28 | 113.3533 | 7485.5173 | Phase3_StableRated | 91.5333 | 8.0326 | 65.8997 | 54.5419 | 57.3003 | 49.8029 | 137.2937 | 25.6454 | 28.7323 | 418.5629 | 45.7659 | 8.3811 | 31.4954 | 0.87058 | 6.6663 | 7.6379 | 11.0609 | 127 | 7 | 22 | 5
500 | 2026-02-14 18:28 | 113.5805 | 7861.6349 | Phase3_StableRated | 92.3041 | 8.0113 | 65.1821 | 54.7338 | 57.4 | 49.9197 | 136.2504 | 25.5506 | 28.6601 | 418.2678 | 45.935 | 8.3548 | 31.5499 | 0.88028 | 6.4054 | 7.6986 | 8.2831 | 127 | 7 | 22 | 5
501 | 2026-02-14 18:28 | 113.8077 | 8030.6599 | Phase3_StableRated | 92.5131 | 8.0268 | 65.7587 | 54.4398 | 57.0584 | 49.8858 | 134.9379 | 25.589 | 28.7308 | 416.627 | 45.8177 | 8.3783 | 31.4074 | 0.87101 | 7.17 | 7.2987 | 11.5918 | 127 | 7 | 22 | 5
502 | 2026-02-14 18:29 | 114.0348 | 7529.3559 | Phase3_StableRated | 92.5401 | 8.0061 | 65.4564 | 54.3984 | 57.665 | 50.0707 | 136.7528 | 25.4814 | 28.7887 | 416.9867 | 45.9464 | 8.3057 | 31.4615 | 0.86412 | 7.0735 | 8.1199 | 9.5847 | 127 | 7 | 22 | 5
503 | 2026-02-14 18:29 | 114.262 | 7851.2001 | Phase3_StableRated | 91.9807 | 7.9757 | 65.9651 | 54.4467 | 57.3549 | 49.5976 | 135.1973 | 25.5597 | 28.8713 | 418.5141 | 45.87 | 8.3214 | 31.525 | 0.87028 | 7.0486 | 7.5473 | 13.2224 | 127 | 7 | 22 | 5
504 | 2026-02-14 18:29 | 114.4891 | 7677.0566 | Phase3_StableRated | 92.05 | 8.049 | 65.6367 | 54.5755 | 57.295 | 49.8327 | 135.841 | 25.4212 | 28.838 | 417.8345 | 46.0148 | 8.2902 | 31.3492 | 0.86726 | 6.1701 | 7.8495 | 13.5564 | 127 | 7 | 22 | 5
505 | 2026-02-14 18:29 | 114.7163 | 7718.0334 | Phase3_StableRated | 92.0949 | 8.0135 | 66.113 | 54.5396 | 57.6263 | 49.6714 | 135.9925 | 25.3775 | 28.5875 | 417.4052 | 46.0242 | 8.3435 | 31.4236 | 0.87169 | 7.4443 | 7.7197 | 9.1094 | 127 | 7 | 22 | 5
506 | 2026-02-14 18:30 | 114.9435 | 7717.0234 | Phase3_StableRated | 91.723 | 8.0293 | 65.8087 | 54.3787 | 57.0479 | 49.8257 | 136.1818 | 25.4493 | 28.6079 | 416.8819 | 46.0023 | 8.3751 | 31.4949 | 0.87389 | 7.264 | 7.742 | 10.5516 | 127 | 7 | 22 | 5
507 | 2026-02-14 18:30 | 115.1706 | 7690.0314 | Phase3_StableRated | 92.3806 | 8.0289 | 65.411 | 54.3927 | 57.6628 | 49.9064 | 135.9612 | 25.4692 | 28.8167 | 417.0293 | 45.9027 | 8.368 | 31.4628 | 0.8685 | 7.1916 | 7.9267 | 10.8577 | 127 | 7 | 22 | 5
508 | 2026-02-14 18:30 | 115.3978 | 7848.0082 | Phase3_StableRated | 93.2558 | 7.9888 | 66.0744 | 54.6398 | 56.9952 | 49.5193 | 134.4405 | 25.6073 | 28.6124 | 416.3133 | 45.9666 | 8.2945 | 31.4244 | 0.8593 | 7.8669 | 8.1149 | 11.8428 | 127 | 7 | 22 | 5
509 | 2026-02-14 18:30 | 115.6249 | 7726.0605 | Phase3_StableRated | 91.6757 | 8.0576 | 65.9095 | 54.448 | 57.7133 | 49.8452 | 135.5128 | 25.413 | 28.6781 | 415.7183 | 45.7099 | 8.4059 | 31.3763 | 0.87494 | 6.9556 | 7.835 | 10.1694 | 127 | 7 | 22 | 5
510 | 2026-02-14 18:31 | 115.8521 | 7913.5444 | Phase3_StableRated | 91.3084 | 8.0362 | 65.7773 | 55.0556 | 57.0588 | 49.8649 | 136.7154 | 25.2853 | 28.6831 | 416.1247 | 46.29 | 8.3605 | 31.4289 | 0.86647 | 7.5609 | 7.8841 | 11.0523 | 127 | 7 | 22 | 5
511 | 2026-02-14 18:31 | 116.0793 | 7878.8828 | Phase3_StableRated | 91.7658 | 7.9786 | 65.63 | 54.0875 | 57.2665 | 49.6879 | 135.8554 | 25.4746 | 28.7624 | 417.2498 | 46.0253 | 8.3865 | 31.4119 | 0.8584 | 7.0799 | 7.8232 | 9.8832 | 127 | 7 | 22 | 5
512 | 2026-02-14 18:31 | 116.3064 | 7864.8384 | Phase3_StableRated | 93.4077 | 7.9808 | 65.3317 | 54.8236 | 56.8178 | 50.0321 | 136.3624 | 25.4399 | 28.4027 | 416.3812 | 45.6806 | 8.3884 | 31.4587 | 0.87159 | 7.3061 | 7.9675 | 10.7757 | 127 | 7 | 22 | 5
513 | 2026-02-14 18:31 | 116.5336 | 7775.8284 | Phase3_StableRated | 91.5564 | 8.0852 | 65.8418 | 54.8652 | 57.1018 | 49.797 | 135.0744 | 25.5413 | 28.8063 | 416.4912 | 46.0159 | 8.3418 | 31.4288 | 0.87165 | 6.521 | 7.6722 | 13.7131 | 127 | 7 | 22 | 5
514 | 2026-02-14 18:32 | 116.7608 | 7842.9351 | Phase3_StableRated | 92.8971 | 7.9244 | 65.5156 | 55.1538 | 56.9259 | 49.8615 | 135.9105 | 25.5759 | 28.6411 | 416.8496 | 45.7895 | 8.3206 | 31.3632 | 0.87888 | 6.7323 | 7.9782 | 12.1768 | 127 | 7 | 22 | 5
515 | 2026-02-14 18:32 | 116.9879 | 8066.4652 | Phase3_StableRated | 92.9146 | 8.1297 | 66.108 | 54.6224 | 57.186 | 49.8431 | 135.107 | 25.6195 | 28.6854 | 416.2349 | 46.0713 | 8.2805 | 31.4037 | 0.86695 | 7.0241 | 7.9822 | 12.372 | 127 | 7 | 22 | 5
516 | 2026-02-14 18:32 | 117.2151 | 8042.1479 | Phase3_StableRated | 91.4779 | 7.9989 | 65.6819 | 54.805 | 57.1553 | 50.0612 | 136.4945 | 25.4169 | 28.7957 | 414.1286 | 46.3264 | 8.3198 | 31.4173 | 0.86828 | 7.2101 | 7.9903 | 12.2709 | 127 | 7 | 22 | 5
517 | 2026-02-14 18:32 | 117.4422 | 7826.6307 | Phase3_StableRated | 92.4675 | 7.9925 | 66.2627 | 54.8208 | 57.6018 | 49.7925 | 135.8521 | 25.4273 | 28.8596 | 416.1495 | 45.9264 | 8.3878 | 31.4972 | 0.87397 | 7.2828 | 7.6243 | 10.149 | 127 | 7 | 22 | 5
518 | 2026-02-14 18:33 | 117.6694 | 8010.2844 | Phase3_StableRated | 92.6603 | 8.0084 | 65.7669 | 54.6986 | 57.3511 | 49.9627 | 136.3776 | 25.3743 | 28.9572 | 415.9575 | 46.0448 | 8.2955 | 31.3794 | 0.88322 | 7.6533 | 7.7614 | 10.9201 | 127 | 7 | 22 | 5
519 | 2026-02-14 18:33 | 117.8966 | 8127.5754 | Phase3_StableRated | 91.758 | 8.011 | 65.8302 | 54.5189 | 57.4054 | 50.0323 | 136.6521 | 25.565 | 28.8316 | 416.5294 | 45.6349 | 8.3256 | 31.4168 | 0.87156 | 5.948 | 7.8161 | 7.7029 | 127 | 7 | 22 | 5
520 | 2026-02-14 18:33 | 118.1237 | 7764.859 | Phase3_StableRated | 91.8208 | 8.0752 | 66.0203 | 54.6994 | 57.1055 | 49.5621 | 136.2387 | 25.6294 | 28.8707 | 417.1747 | 46.1593 | 8.3962 | 31.4102 | 0.86176 | 6.179 | 7.4981 | 13.5873 | 127 | 7 | 22 | 5
521 | 2026-02-14 18:33 | 118.3509 | 8125.9475 | Phase3_StableRated | 91.8455 | 8.0044 | 65.8769 | 54.0532 | 57.0265 | 49.8679 | 135.7723 | 25.5606 | 28.6819 | 415.849 | 45.7153 | 8.2881 | 31.4046 | 0.87233 | 6.8783 | 8.1033 | 3.2743 | 127 | 7 | 22 | 5
522 | 2026-02-14 18:34 | 118.578 | 7952.9955 | Phase3_StableRated | 91.4785 | 8.0289 | 66.1295 | 54.6423 | 57.8147 | 49.7951 | 134.9818 | 25.4263 | 28.6433 | 415.9402 | 45.9188 | 8.3184 | 31.3098 | 0.86419 | 6.465 | 7.758 | 10.3801 | 127 | 7 | 22 | 5
523 | 2026-02-14 18:34 | 118.8052 | 8161.0702 | Phase3_StableRated | 91.7932 | 8.0205 | 65.899 | 54.6318 | 57.0912 | 50.0747 | 135.7938 | 25.6578 | 28.7697 | 415.3629 | 45.8192 | 8.3381 | 31.4227 | 0.86835 | 9.1465 | 7.8248 | 13.4604 | 127 | 7 | 22 | 5
524 | 2026-02-14 18:34 | 119.0324 | 7968.1431 | Phase3_StableRated | 91.3775 | 8.004 | 65.5342 | 54.6276 | 57.6341 | 49.523 | 135.4786 | 25.491 | 28.7564 | 415.758 | 46.0463 | 8.3586 | 31.3379 | 0.87075 | 7.3659 | 7.643 | 7.1315 | 127 | 7 | 22 | 5
525 | 2026-02-14 18:34 | 119.2595 | 7820.8659 | Phase3_StableRated | 91.9947 | 8.042 | 66.0859 | 54.9681 | 57.3189 | 50.4447 | 135.3144 | 25.551 | 28.6393 | 415.2683 | 46.0337 | 8.2661 | 31.3555 | 0.85551 | 6.7212 | 7.5128 | 11.3649 | 127 | 7 | 22 | 5
526 | 2026-02-14 18:34 | 119.4867 | 7864.0019 | Phase3_StableRated | 91.4557 | 7.9895 | 66.3393 | 54.4248 | 57.3815 | 50.0975 | 135.5425 | 25.3905 | 28.8043 | 414.8591 | 45.8751 | 8.3438 | 31.5029 | 0.86766 | 6.6336 | 7.6663 | 8.5491 | 127 | 7 | 22 | 5
527 | 2026-02-14 18:35 | 119.7138 | 8141.1844 | Phase3_StableRated | 92.0245 | 8.0296 | 65.6009 | 54.5581 | 57.4501 | 49.8295 | 134.7125 | 25.506 | 28.6809 | 416.4099 | 45.8186 | 8.3537 | 31.4057 | 0.87208 | 6.4017 | 7.8365 | 9.3442 | 127 | 7 | 22 | 5
528 | 2026-02-14 18:35 | 119.941 | 8189.678 | Phase3_StableRated | 91.1666 | 7.9994 | 65.8113 | 54.816 | 57.7173 | 50.1677 | 133.847 | 25.3584 | 28.5911 | 415.7269 | 46.2307 | 8.3496 | 31.3891 | 0.86982 | 6.698 | 7.9375 | 12.6223 | 127 | 7 | 22 | 5
529 | 2026-02-14 18:35 | 120.1682 | 8023.2782 | Phase3_StableRated | 92.178 | 7.9512 | 66.1169 | 54.5439 | 57.3839 | 50.287 | 134.7852 | 25.3312 | 28.7244 | 416.6954 | 45.7198 | 8.3361 | 31.4324 | 0.88132 | 6.6426 | 7.8023 | 11.1024 | 127 | 7 | 22 | 5
530 | 2026-02-14 18:36 | 120.3953 | 8279.7289 | Phase3_StableRated | 92.302 | 8.0378 | 65.8757 | 54.5992 | 57.3135 | 50.1238 | 135.897 | 25.4029 | 28.7463 | 414.5442 | 45.619 | 8.3772 | 31.2551 | 0.87503 | 6.5786 | 7.8671 | 5.0701 | 127 | 7 | 22 | 5
531 | 2026-02-14 18:36 | 120.6225 | 7935.8638 | Phase3_StableRated | 91.135 | 8.0245 | 65.9621 | 54.73 | 57.2259 | 50.241 | 134.698 | 25.427 | 28.7986 | 415.0074 | 46.0578 | 8.3617 | 31.33 | 0.85784 | 6.7681 | 7.668 | 8.5253 | 127 | 7 | 22 | 5
532 | 2026-02-14 18:36 | 120.8497 | 8200.5203 | Phase3_StableRated | 92.1978 | 8.0161 | 66.4431 | 54.7535 | 57.4047 | 50.0248 | 135.4272 | 25.4395 | 28.4581 | 412.9357 | 45.8131 | 8.311 | 31.1975 | 0.87728 | 7.5092 | 7.8989 | 12.7839 | 127 | 7 | 22 | 5
533 | 2026-02-14 18:36 | 121.0768 | 8037.1046 | Phase3_StableRated | 92.4275 | 7.9655 | 66.3375 | 54.7961 | 57.603 | 50.0748 | 137.0197 | 25.3006 | 28.6188 | 413.6107 | 46.1788 | 8.3153 | 31.3274 | 0.87228 | 7.5504 | 8.1062 | 11.3875 | 127 | 7 | 22 | 5
534 | 2026-02-14 18:36 | 121.304 | 8139.8876 | Phase3_StableRated | 91.5454 | 8.0575 | 65.6336 | 54.4561 | 57.3998 | 49.9936 | 136.2477 | 25.5316 | 28.65 | 414.8264 | 45.9403 | 8.2228 | 31.4811 | 0.8692 | 6.7748 | 7.9375 | 14.8409 | 127 | 7 | 22 | 5
535 | 2026-02-14 18:37 | 121.5311 | 8264.5485 | Phase3_StableRated | 92.5659 | 8.0468 | 66.0747 | 54.6264 | 57.4603 | 49.7998 | 136.9906 | 25.5541 | 28.7352 | 413.7186 | 46.0867 | 8.3522 | 31.3791 | 0.87936 | 5.9042 | 7.9315 | 15.0295 | 127 | 7 | 22 | 5
536 | 2026-02-14 18:37 | 121.7583 | 8138.1737 | Phase3_StableRated | 92.2229 | 8.0293 | 66.3682 | 54.5553 | 57.7304 | 49.979 | 135.5342 | 25.1957 | 28.8206 | 414.3115 | 46.3149 | 8.322 | 31.3995 | 0.87304 | 6.8168 | 7.8972 | 8.974 | 127 | 7 | 22 | 5
537 | 2026-02-14 18:37 | 121.9855 | 8227.941 | Phase3_StableRated | 91.4934 | 8.0336 | 66.2141 | 54.8518 | 57.5091 | 49.8441 | 136.766 | 25.5673 | 28.7268 | 414.0075 | 45.8179 | 8.3851 | 31.2874 | 0.87486 | 7.9444 | 7.475 | 16.9357 | 127 | 7 | 22 | 5
538 | 2026-02-14 18:37 | 122.2126 | 8460.6384 | Phase3_StableRated | 92.1467 | 7.9571 | 66.3038 | 54.7961 | 57.2826 | 50.1458 | 134.7659 | 25.3332 | 28.4954 | 413.2568 | 46.0658 | 8.2489 | 31.2985 | 0.86646 | 7.4909 | 7.5816 | 10.4523 | 127 | 7 | 22 | 5
539 | 2026-02-14 18:38 | 122.4398 | 8228.7642 | Phase3_StableRated | 92.3518 | 7.9592 | 66.7597 | 54.7932 | 57.0143 | 49.7684 | 134.9332 | 25.5703 | 28.5807 | 414.8836 | 46.0588 | 8.2756 | 31.242 | 0.8657 | 7.153 | 7.9076 | 7.7114 | 127 | 7 | 22 | 5
540 | 2026-02-14 18:38 | 122.6669 | 8464.8568 | Phase3_StableRated | 91.7982 | 8.0436 | 66.195 | 54.3194 | 56.7744 | 49.9453 | 133.0543 | 25.3971 | 28.8082 | 414.7782 | 46.2467 | 8.3268 | 31.4306 | 0.87565 | 7.5032 | 7.8289 | 8.3561 | 127 | 7 | 22 | 5
541 | 2026-02-14 18:38 | 122.8941 | 8173.2771 | Phase3_StableRated | 92.3615 | 7.9981 | 65.7416 | 54.8937 | 57.345 | 50.1196 | 136.5933 | 25.3883 | 28.4122 | 415.4238 | 46.1324 | 8.3291 | 31.3235 | 0.86905 | 6.809 | 7.8611 | 4.9705 | 127 | 7 | 22 | 5
542 | 2026-02-14 18:38 | 123.1213 | 8447.9421 | Phase3_StableRated | 91.1454 | 7.9958 | 66.4213 | 54.7306 | 57.5001 | 50.079 | 137.0281 | 25.3246 | 28.5789 | 413.0848 | 46.0022 | 8.2767 | 31.3409 | 0.8778 | 7.2966 | 8.1228 | 14.7668 | 127 | 7 | 22 | 5
543 | 2026-02-14 18:39 | 123.3484 | 8605.8021 | Phase3_StableRated | 92.1371 | 8.0302 | 66.2387 | 55.0151 | 57.0989 | 50.0081 | 135.2676 | 25.6178 | 28.5892 | 413.318 | 46.2419 | 8.2727 | 31.2362 | 0.86633 | 6.426 | 7.8965 | 15.1415 | 127 | 7 | 22 | 5
544 | 2026-02-14 18:39 | 123.5756 | 8009.9558 | Phase3_StableRated | 91.1787 | 8.0721 | 66.0455 | 54.8029 | 57.4075 | 50.6166 | 135.3882 | 25.3776 | 28.4468 | 412.8708 | 45.984 | 8.3291 | 31.2996 | 0.8712 | 6.9635 | 8.027 | 8.2137 | 127 | 7 | 22 | 5
545 | 2026-02-14 18:39 | 123.8027 | 8287.0011 | Phase3_StableRated | 91.724 | 8.0252 | 66.1139 | 54.8302 | 57.4464 | 50.2616 | 135.0189 | 25.5284 | 28.8407 | 412.7632 | 46.0197 | 8.3962 | 31.2011 | 0.8733 | 7.6832 | 7.8009 | 10.0845 | 127 | 7 | 22 | 5
546 | 2026-02-14 18:40 | 124.0299 | 8517.0615 | Phase3_StableRated | 91.5919 | 7.9543 | 66.2977 | 54.8394 | 57.733 | 49.9485 | 135.9073 | 25.5547 | 28.8648 | 413.8859 | 45.881 | 8.2398 | 31.2725 | 0.87469 | 6.3746 | 7.6394 | 10.6351 | 127 | 7 | 22 | 5
547 | 2026-02-14 18:40 | 124.2571 | 8410.6338 | Phase3_StableRated | 91.646 | 8.0854 | 65.8821 | 55.0878 | 57.5183 | 50.0073 | 136.5784 | 25.4466 | 28.4568 | 415.1449 | 46.532 | 8.2878 | 31.2784 | 0.87527 | 6.2366 | 7.7795 | 8.1161 | 127 | 7 | 22 | 5
548 | 2026-02-14 18:40 | 124.4842 | 8515.7617 | Phase3_StableRated | 92.5825 | 8.0085 | 66.4377 | 54.6553 | 57.3057 | 50.0004 | 134.2078 | 25.6701 | 28.6575 | 412.6406 | 45.7313 | 8.4059 | 31.3015 | 0.88058 | 6.8848 | 7.6565 | 5.7223 | 127 | 7 | 22 | 5
549 | 2026-02-14 18:40 | 124.7114 | 8378.8711 | Phase3_StableRated | 92.5176 | 8.0542 | 66.147 | 54.7453 | 57.65 | 49.9024 | 135.5731 | 25.3264 | 28.3571 | 412.7228 | 45.9735 | 8.3026 | 31.2543 | 0.86036 | 6.3325 | 8.1332 | 9.7848 | 127 | 7 | 22 | 5
550 | 2026-02-14 18:40 | 124.9385 | 8502.1792 | Phase3_StableRated | 92.2821 | 8.0854 | 65.885 | 55.0944 | 57.3655 | 49.8957 | 135.4258 | 25.5672 | 28.409 | 412.5634 | 46.1733 | 8.3056 | 31.2578 | 0.87309 | 7.2431 | 7.9146 | 10.2787 | 127 | 7 | 22 | 5
551 | 2026-02-14 18:41 | 125.1657 | 8479.7688 | Phase3_StableRated | 91.2801 | 8.0313 | 66.2235 | 54.8272 | 57.6309 | 50.2947 | 135.4562 | 25.4335 | 28.6843 | 412.0378 | 46.4147 | 8.3388 | 31.2195 | 0.87598 | 6.2862 | 7.8955 | 9.6685 | 127 | 7 | 22 | 5
552 | 2026-02-14 18:41 | 125.3929 | 8701.9393 | Phase3_StableRated | 91.8183 | 8.0359 | 65.2375 | 54.7644 | 57.5174 | 50.0622 | 135.9052 | 25.6121 | 28.6431 | 411.7017 | 45.8671 | 8.3296 | 31.2658 | 0.8819 | 7.8397 | 8.0636 | 10.9799 | 127 | 7 | 22 | 5
553 | 2026-02-14 18:41 | 125.62 | 8574.6977 | Phase3_StableRated | 92.2478 | 8.0829 | 66.3293 | 54.5095 | 57.2067 | 50.2131 | 135.4607 | 25.3939 | 28.724 | 413.3284 | 46.5313 | 8.2525 | 31.2947 | 0.87375 | 5.938 | 7.3825 | 14.2489 | 127 | 7 | 22 | 5
554 | 2026-02-14 18:41 | 125.8472 | 8603.1254 | Phase3_StableRated | 91.4596 | 7.969 | 66.5819 | 54.5717 | 57.4011 | 50.3648 | 135.3363 | 25.3624 | 28.4072 | 413.3227 | 46.4457 | 8.3507 | 31.2414 | 0.8698 | 7.4558 | 7.9135 | 9.8781 | 127 | 7 | 22 | 5
555 | 2026-02-14 18:42 | 126.0744 | 8501.4837 | Phase3_StableRated | 93.1674 | 8.0054 | 65.7208 | 54.7724 | 57.4082 | 50.4944 | 135.4294 | 25.4945 | 28.7796 | 412.5836 | 46.2323 | 8.2611 | 31.2717 | 0.86325 | 6.2747 | 7.5327 | 10.9975 | 127 | 7 | 22 | 5
556 | 2026-02-14 18:42 | 126.3015 | 8505.088 | Phase3_StableRated | 92.1505 | 8.0383 | 65.9257 | 54.7094 | 57.5578 | 50.0621 | 136.2989 | 25.3388 | 28.5829 | 412.6088 | 46.1182 | 8.2931 | 31.2666 | 0.86398 | 5.5036 | 7.802 | 12.4099 | 127 | 7 | 22 | 5
557 | 2026-02-14 18:42 | 126.5287 | 8529.1209 | Phase3_StableRated | 91.8852 | 8.0236 | 66.5575 | 54.6013 | 57.5375 | 50.1955 | 135.5408 | 25.2989 | 28.6553 | 410.3629 | 46.1593 | 8.3302 | 31.2038 | 0.87626 | 6.6065 | 7.7563 | 11.7732 | 127 | 7 | 22 | 5
558 | 2026-02-14 18:42 | 126.7558 | 8673.7415 | Phase3_StableRated | 91.5598 | 7.9761 | 65.7927 | 54.7786 | 57.1171 | 50.5056 | 135.5855 | 25.35 | 28.4968 | 411.7088 | 46.1059 | 8.2487 | 31.2217 | 0.86676 | 6.4476 | 7.9067 | 9.4121 | 127 | 7 | 22 | 5
559 | 2026-02-14 18:43 | 126.983 | 8561.7966 | Phase3_StableRated | 92.1476 | 8.0177 | 65.8156 | 54.9074 | 57.6283 | 50.1892 | 134.3576 | 25.4399 | 28.4562 | 412.2956 | 46.3884 | 8.2665 | 31.2231 | 0.87044 | 5.8993 | 7.8473 | 10.8774 | 127 | 7 | 22 | 5
560 | 2026-02-14 18:43 | 127.2102 | 8688.2578 | Phase3_StableRated | 91.7212 | 7.9684 | 66.531 | 54.9604 | 57.6492 | 50.1251 | 135.0389 | 25.595 | 28.3764 | 411.3339 | 45.8344 | 8.3864 | 31.1975 | 0.87118 | 5.4733 | 8.0554 | 12.3066 | 127 | 7 | 22 | 5
561 | 2026-02-14 18:43 | 127.4373 | 8982.623 | Phase3_StableRated | 92.1535 | 7.982 | 66.8689 | 54.4311 | 57.4147 | 50.5356 | 136.3294 | 25.4137 | 28.6706 | 412.1324 | 46.1515 | 8.3933 | 31.2607 | 0.87634 | 6.7499 | 7.6488 | 8.1249 | 127 | 7 | 22 | 5
562 | 2026-02-14 18:43 | 127.6645 | 8809.9378 | Phase3_StableRated | 92.2254 | 7.9259 | 66.4226 | 54.6687 | 57.5704 | 50.1302 | 135.2863 | 25.5841 | 28.7194 | 412.7167 | 46.0344 | 8.3091 | 31.1666 | 0.87118 | 7.1417 | 7.9687 | 13.6203 | 127 | 7 | 22 | 5
563 | 2026-02-14 18:44 | 127.8916 | 8638.3661 | Phase3_StableRated | 91.5808 | 8.0342 | 66.2371 | 54.7485 | 57.5826 | 50.3994 | 135.8503 | 25.2894 | 28.7488 | 411.6026 | 45.9631 | 8.3333 | 31.2203 | 0.86379 | 6.9196 | 7.84 | 14.2712 | 127 | 7 | 22 | 5
564 | 2026-02-14 18:44 | 128.1188 | 8892.3687 | Phase3_StableRated | 90.8435 | 8.0154 | 66.6678 | 54.4791 | 57.4579 | 50.0067 | 136.9646 | 25.2855 | 28.6719 | 411.892 | 46.5467 | 8.3642 | 31.2374 | 0.86794 | 6.7222 | 7.4661 | 8.8406 | 127 | 7 | 22 | 5
565 | 2026-02-14 18:44 | 128.346 | 8656.4166 | Phase3_StableRated | 90.8822 | 8.0196 | 66.0244 | 54.6096 | 57.1468 | 50.0962 | 136.4361 | 25.3851 | 28.6816 | 411.2398 | 46.1226 | 8.3488 | 31.176 | 0.87476 | 7.0625 | 7.618 | 11.1369 | 127 | 7 | 22 | 5
566 | 2026-02-14 18:44 | 128.5731 | 8417.2217 | Phase3_StableRated | 92.0206 | 7.959 | 66.0373 | 54.6977 | 57.3703 | 50.2158 | 135.7567 | 25.4299 | 28.3438 | 411.9862 | 46.4272 | 8.3022 | 31.122 | 0.89002 | 6.8157 | 7.7455 | 12.6745 | 127 | 7 | 22 | 5
567 | 2026-02-14 18:45 | 128.8003 | 8593.5572 | Phase3_StableRated | 91.2655 | 8.0116 | 66.6269 | 54.4772 | 57.3449 | 50.3821 | 134.9016 | 25.439 | 28.5246 | 411.5272 | 45.7313 | 8.2931 | 31.1947 | 0.86458 | 5.6175 | 8.022 | 9.4301 | 127 | 7 | 22 | 5
568 | 2026-02-14 18:45 | 129.0274 | 8474.2285 | Phase3_StableRated | 90.8397 | 7.9736 | 66.5255 | 54.6608 | 57.2653 | 50.1189 | 132.8888 | 25.4188 | 28.5985 | 409.9988 | 46.4322 | 8.3622 | 31.2855 | 0.87757 | 5.3811 | 7.9179 | 11.7108 | 127 | 7 | 22 | 5
569 | 2026-02-14 18:45 | 129.2546 | 8726.9878 | Phase3_StableRated | 91.9868 | 8.0405 | 66.3523 | 54.9372 | 57.4899 | 50.3586 | 135.5581 | 25.3464 | 28.8638 | 410.5831 | 46.6461 | 8.3386 | 31.3091 | 0.86457 | 6.7155 | 7.548 | 11.3536 | 127 | 7 | 22 | 5
570 | 2026-02-14 18:46 | 129.4818 | 8800.2085 | Phase3_StableRated | 93.1115 | 7.9681 | 65.8698 | 54.2154 | 57.4678 | 49.9218 | 135.0897 | 25.498 | 28.6715 | 410.0074 | 46.2266 | 8.3286 | 31.1546 | 0.88341 | 6.4782 | 7.7709 | 7.0422 | 127 | 7 | 22 | 5
571 | 2026-02-14 18:46 | 129.7089 | 9074.6404 | Phase3_StableRated | 91.5703 | 7.9324 | 66.7071 | 55.2271 | 57.6051 | 50.1661 | 135.9677 | 25.4638 | 28.8005 | 411.8415 | 46.5948 | 8.2821 | 31.205 | 0.8733 | 7.3641 | 8.2031 | 12.1137 | 127 | 7 | 22 | 5
572 | 2026-02-14 18:46 | 129.9361 | 8879.2683 | Phase3_StableRated | 92.2053 | 8.0199 | 66.2534 | 55.2363 | 57.5881 | 50.4092 | 135.4698 | 25.32 | 28.7778 | 412.008 | 46.2001 | 8.2258 | 31.1163 | 0.88399 | 7.2683 | 7.8415 | 7.7742 | 127 | 7 | 22 | 5
573 | 2026-02-14 18:46 | 130.1633 | 8809.4076 | Phase3_StableRated | 91.7339 | 8.0056 | 66.1736 | 54.8012 | 57.8155 | 50.3877 | 134.9724 | 25.4269 | 28.4959 | 411.6602 | 45.9475 | 8.3231 | 31.1869 | 0.872 | 6.8861 | 7.7429 | 13.1118 | 127 | 7 | 22 | 5
574 | 2026-02-14 18:47 | 130.3904 | 8988.6279 | Phase3_StableRated | 91.8313 | 8.0307 | 66.254 | 54.8335 | 57.4727 | 50.3375 | 133.7466 | 25.3616 | 28.6187 | 409.7279 | 46.1667 | 8.315 | 31.1119 | 0.87857 | 6.2979 | 7.9157 | 8.9456 | 127 | 7 | 22 | 5
575 | 2026-02-14 18:47 | 130.6176 | 8529.1011 | Phase3_StableRated | 92.2896 | 7.9897 | 66.5131 | 54.6527 | 57.4327 | 50.0787 | 134.5564 | 25.409 | 28.589 | 410.5329 | 46.5371 | 8.3149 | 31.1532 | 0.87212 | 5.6604 | 7.954 | 10.482 | 127 | 7 | 22 | 5
576 | 2026-02-14 18:47 | 130.8447 | 8926.7401 | Phase3_StableRated | 91.6276 | 8.0554 | 66.552 | 54.9744 | 57.5089 | 50.1136 | 135.6536 | 25.4176 | 28.4463 | 409.4874 | 46.1843 | 8.3154 | 31.2284 | 0.87329 | 6.7717 | 7.7122 | 14.3159 | 127 | 7 | 22 | 5
577 | 2026-02-14 18:47 | 131.0719 | 9025.7851 | Phase3_StableRated | 92.0053 | 7.9771 | 66.321 | 55.1741 | 57.2946 | 50.1399 | 137.1848 | 25.4547 | 28.5855 | 411.6268 | 46.0701 | 8.3205 | 31.0978 | 0.88169 | 7.2369 | 7.8994 | 12.2075 | 127 | 7 | 22 | 5
578 | 2026-02-14 18:48 | 131.2991 | 8689.8338 | Phase3_StableRated | 91.874 | 8.0808 | 66.205 | 54.8874 | 57.3298 | 50.2486 | 135.1446 | 25.2764 | 28.5825 | 410.2181 | 46.3558 | 8.3084 | 31.269 | 0.87557 | 4.9073 | 7.7519 | 7.9047 | 127 | 7 | 22 | 5
579 | 2026-02-14 18:48 | 131.5262 | 9114.9016 | Phase3_StableRated | 91.3223 | 8.0053 | 66.3443 | 55.0644 | 57.4463 | 50.4444 | 136.0281 | 25.5607 | 28.8428 | 410.8112 | 46.3609 | 8.3741 | 31.1862 | 0.87322 | 6.3448 | 7.9442 | 8.3659 | 127 | 7 | 22 | 5
580 | 2026-02-14 18:48 | 131.7534 | 9004.5468 | Phase3_StableRated | 91.9658 | 8.0582 | 66.2484 | 54.8111 | 57.6112 | 50.2131 | 136.0233 | 25.2909 | 28.3156 | 410.1323 | 46.4559 | 8.2762 | 31.1182 | 0.87293 | 6.0248 | 7.8493 | 9.2201 | 127 | 7 | 22 | 5
581 | 2026-02-14 18:48 | 131.9805 | 8902.2326 | Phase3_StableRated | 91.7349 | 7.9984 | 65.6004 | 54.4859 | 58.0762 | 50.2532 | 134.3535 | 25.3152 | 28.8445 | 411.3517 | 46.4945 | 8.332 | 31.099 | 0.87167 | 6.4007 | 7.9513 | 11.3027 | 127 | 7 | 22 | 5
582 | 2026-02-14 18:49 | 132.2077 | 9081.3848 | Phase3_StableRated | 91.4411 | 7.9164 | 66.2279 | 54.6191 | 57.5468 | 50.4539 | 135.343 | 25.7302 | 28.5782 | 409.352 | 46.3128 | 8.3541 | 31.1912 | 0.88079 | 5.7997 | 7.7007 | 11.1758 | 127 | 7 | 22 | 5
583 | 2026-02-14 18:49 | 132.4349 | 9352.6756 | Phase3_StableRated | 92.104 | 8.0194 | 66.3273 | 54.9193 | 57.4442 | 50.205 | 134.635 | 25.2918 | 28.429 | 411.4211 | 46.2765 | 8.2755 | 31.1993 | 0.88311 | 6.4735 | 7.6521 | 8.5648 | 127 | 7 | 22 | 5
584 | 2026-02-14 18:49 | 132.662 | 9041.8154 | Phase3_StableRated | 91.2777 | 8.0935 | 66.0945 | 54.8439 | 57.5982 | 50.2754 | 135.736 | 25.2444 | 28.8392 | 410.5899 | 46.3251 | 8.3303 | 31.1553 | 0.87453 | 6.172 | 8.0487 | 7.3229 | 127 | 7 | 22 | 5
585 | 2026-02-14 18:49 | 132.8892 | 9067.6145 | Phase3_StableRated | 92.0024 | 8.0322 | 66.2973 | 54.7813 | 57.5861 | 50.663 | 135.1037 | 25.4595 | 28.8054 | 409.9378 | 46.1901 | 8.2596 | 31.202 | 0.86665 | 6.1766 | 7.8477 | 10.9279 | 127 | 7 | 22 | 5
586 | 2026-02-14 18:50 | 133.1163 | 8972.5176 | Phase3_StableRated | 91.7134 | 8.0242 | 66.136 | 54.9055 | 57.5151 | 50.6061 | 135.3285 | 25.1848 | 28.7729 | 409.312 | 46.5415 | 8.2792 | 31.2205 | 0.86797 | 5.8911 | 7.8907 | 10.1526 | 127 | 7 | 22 | 5
587 | 2026-02-14 18:50 | 133.3435 | 8926.9543 | Phase3_StableRated | 92.6617 | 8.0056 | 66.8131 | 54.7251 | 57.9024 | 50.3842 | 134.9251 | 25.4061 | 28.6804 | 410.9848 | 46.2751 | 8.2991 | 31.1625 | 0.87068 | 6.3348 | 7.7334 | 16.5989 | 127 | 7 | 22 | 5
588 | 2026-02-14 18:50 | 133.5707 | 9204.848 | Phase3_StableRated | 92.0321 | 8.1164 | 66.7631 | 54.6835 | 56.8995 | 50.333 | 135.818 | 25.7131 | 28.9382 | 409.9073 | 46.6258 | 8.3973 | 30.97 | 0.8832 | 5.7686 | 8.0253 | 10.6306 | 127 | 7 | 22 | 5
589 | 2026-02-14 18:50 | 133.7978 | 8956.8475 | Phase3_StableRated | 91.6905 | 8.0225 | 66.283 | 54.6258 | 57.0276 | 50.4648 | 137.2131 | 25.263 | 28.7488 | 410.0367 | 46.236 | 8.3127 | 31.2495 | 0.87691 | 6.9214 | 7.705 | 15.3328 | 127 | 7 | 22 | 5
590 | 2026-02-14 18:50 | 134.025 | 9117.189 | Phase3_StableRated | 92.1925 | 8.0216 | 66.2507 | 54.7011 | 57.4682 | 50.7064 | 134.2246 | 25.2676 | 28.5121 | 409.6834 | 46.1729 | 8.3502 | 31.1894 | 0.8658 | 6.7268 | 7.7874 | 7.8934 | 127 | 7 | 22 | 5
591 | 2026-02-14 18:51 | 134.2521 | 9046.8291 | Phase3_StableRated | 92.5369 | 8.0662 | 66.3224 | 54.7754 | 57.8354 | 50.4618 | 135.247 | 25.26 | 28.5594 | 410.6864 | 46.3056 | 8.3589 | 31.1552 | 0.87366 | 6.2106 | 7.9464 | 7.2521 | 127 | 7 | 22 | 5
592 | 2026-02-14 18:51 | 134.4793 | 9211.6986 | Phase3_StableRated | 92.1711 | 8.0301 | 66.3572 | 55.1105 | 57.336 | 50.6544 | 135.3505 | 25.5349 | 28.7485 | 409.77 | 46.1746 | 8.3028 | 31.1522 | 0.87122 | 7.4227 | 8.066 | 7.9223 | 127 | 7 | 22 | 5
593 | 2026-02-14 18:51 | 134.7065 | 9204.4325 | Phase3_StableRated | 92.1107 | 8.1249 | 66.2422 | 54.2949 | 56.9478 | 50.6583 | 135.9166 | 25.5587 | 28.611 | 410.1588 | 46.0115 | 8.29 | 31.1632 | 0.87189 | 6.297 | 7.7464 | 13.4912 | 127 | 7 | 22 | 5
594 | 2026-02-14 18:52 | 134.9336 | 9329.8187 | Phase3_StableRated | 91.161 | 7.9957 | 66.0401 | 54.9588 | 57.6674 | 50.7444 | 134.8597 | 25.4189 | 28.5624 | 410.0522 | 46.2446 | 8.3141 | 31.0633 | 0.88355 | 7.5626 | 8.2351 | 15.2096 | 127 | 7 | 22 | 5
595 | 2026-02-14 18:52 | 135.1608 | 9103.5099 | Phase3_StableRated | 91.3748 | 8.0407 | 66.1064 | 55.1125 | 57.5652 | 50.7009 | 132.9439 | 25.4777 | 28.6124 | 410.9761 | 46.4956 | 8.316 | 31.2246 | 0.87191 | 6.1204 | 7.9006 | 8.6939 | 127 | 7 | 22 | 5
596 | 2026-02-14 18:52 | 135.388 | 9156.4562 | Phase3_StableRated | 91.8008 | 8.0298 | 66.4101 | 54.763 | 57.3923 | 50.6015 | 136.471 | 25.5323 | 28.2781 | 410.0972 | 46.4482 | 8.3795 | 31.0843 | 0.8656 | 5.2321 | 7.5953 | 9.8707 | 127 | 7 | 22 | 5
597 | 2026-02-14 18:52 | 135.6151 | 9061.1551 | Phase3_StableRated | 91.5708 | 7.9457 | 66.3567 | 54.1854 | 57.5175 | 50.716 | 136.0937 | 25.5806 | 28.6224 | 408.5781 | 46.4979 | 8.3126 | 31.098 | 0.88428 | 6.9246 | 7.8921 | 7.9807 | 127 | 7 | 22 | 5
598 | 2026-02-14 18:53 | 135.8423 | 9160.0783 | Phase3_StableRated | 92.0122 | 8.0301 | 66.0086 | 54.8096 | 57.5875 | 50.5225 | 133.6759 | 25.4252 | 28.305 | 411.6426 | 46.2807 | 8.3 | 31.0926 | 0.88212 | 6.5654 | 7.7429 | 6.29 | 127 | 7 | 22 | 5
599 | 2026-02-14 18:53 | 136.0694 | 9303.8528 | Phase3_StableRated | 91.8014 | 8.0524 | 66.5797 | 54.8428 | 57.5208 | 50.286 | 134.6358 | 25.1497 | 28.5945 | 409.9033 | 46.1966 | 8.4032 | 31.1549 | 0.88119 | 6.4344 | 7.9199 | 12.6568 | 127 | 7 | 22 | 5
600 | 2026-02-14 18:53 | 136.2966 | 9378.5975 | Phase3_StableRated | 92.0041 | 8.0371 | 66.2842 | 54.7215 | 57.627 | 50.418 | 136.6105 | 25.2868 | 28.7878 | 409.2608 | 46.0789 | 8.3051 | 31.2179 | 0.8761 | 6.1144 | 7.8368 | 11.2207 | 127 | 7 | 22 | 5
601 | 2026-02-14 18:53 | 136.5238 | 9131.7319 | Phase4_UnloadCycle | 91.6021 | 8.1906 | 66.4571 | 54.7423 | 57.708 | 50.4547 | 133.6302 | 25.3571 | 28.5796 | 409.0865 | 46.4294 | 8.2591 | 31.2238 | 0.86972 | 4.2457 | 8.0174 | 8.7372 | 127 | 7 | 22 | 5
602 | 2026-02-14 18:54 | 136.7509 | 9427.0572 | Phase4_UnloadCycle | 92.0345 | 8.2388 | 66.6735 | 55.2753 | 57.0313 | 50.4594 | 130.4186 | 25.463 | 28.8594 | 410.469 | 46.6017 | 8.3212 | 31.0873 | 0.88216 | 1.7392 | 7.982 | 3.0642 | 127 | 7 | 22 | 5
603 | 2026-02-14 18:54 | 136.9781 | 9518.4138 | Phase4_UnloadCycle | 91.5403 | 8.4618 | 66.4725 | 55.0927 | 57.269 | 50.5423 | 127.5973 | 25.3787 | 28.4335 | 409.4306 | 46.5908 | 8.3124 | 31.0527 | 0.87986 | 0.38736 | 8.4851 | 9.4414 | 127 | 7 | 22 | 5
604 | 2026-02-14 18:54 | 137.2052 | 9386.6669 | Phase4_UnloadCycle | 90.8881 | 8.4209 | 66.5604 | 54.7024 | 57.3653 | 50.7273 | 124.7547 | 25.5721 | 28.7827 | 409.3501 | 46.5598 | 8.2616 | 31.0639 | 0.87761 | -1.2688 | 8.2435 | 1.4981 | 127 | 7 | 22 | 5
605 | 2026-02-14 18:54 | 137.4324 | 9630.6913 | Phase4_UnloadCycle | 91.2298 | 8.5177 | 66.2614 | 54.4661 | 57.511 | 50.1696 | 122.8802 | 25.6224 | 28.7428 | 407.3437 | 46.5169 | 8.2922 | 31.0357 | 0.86299 | -3.0371 | 8.3752 | 2.6417 | 127 | 7 | 22 | 5
606 | 2026-02-14 18:54 | 137.6596 | 9232.0792 | Phase4_UnloadCycle | 91.8451 | 8.6004 | 66.2573 | 54.7975 | 57.5457 | 50.7717 | 121.8486 | 25.3979 | 28.3823 | 409.4772 | 46.7378 | 8.3787 | 31.0477 | 0.88514 | -4.3964 | 8.8083 | -4.0558 | 127 | 7 | 22 | 5
607 | 2026-02-14 18:55 | 137.8867 | 9173.9596 | Phase4_UnloadCycle | 91.2479 | 8.4986 | 66.3405 | 55.0092 | 57.7263 | 50.6489 | 118.3561 | 25.588 | 29.0347 | 409.034 | 46.4037 | 8.3083 | 31.0255 | 0.87843 | -6.383 | 9.2142 | -2.7114 | 127 | 7 | 22 | 5
608 | 2026-02-14 18:55 | 138.1139 | 9105.9675 | Phase4_UnloadCycle | 91.9572 | 8.4567 | 66.3359 | 54.9346 | 57.2691 | 50.4748 | 116.8968 | 25.4987 | 28.627 | 410.784 | 46.486 | 8.3086 | 31.1569 | 0.8715 | -7.6506 | 8.9117 | -2.6926 | 127 | 7 | 22 | 5
609 | 2026-02-14 18:55 | 138.341 | 9632.9501 | Phase4_UnloadCycle | 92.9371 | 8.3528 | 66.504 | 54.8107 | 57.7267 | 50.5712 | 117.6052 | 25.4845 | 28.6208 | 409.2631 | 46.4511 | 8.4009 | 31.1373 | 0.88048 | -8.8202 | 9.2194 | -3.7312 | 127 | 7 | 22 | 5
610 | 2026-02-14 18:56 | 138.5682 | 9516.906 | Phase4_UnloadCycle | 92.3451 | 8.2938 | 66.0358 | 54.9696 | 57.6933 | 50.6574 | 116.1834 | 25.5599 | 28.3619 | 408.8804 | 46.0802 | 8.3909 | 31.0881 | 0.88188 | -8.7314 | 9.2792 | -3.9521 | 127 | 7 | 22 | 5
611 | 2026-02-14 18:56 | 138.7954 | 9421.439 | Phase4_UnloadCycle | 91.5892 | 8.17 | 66.1988 | 55.2168 | 58.0937 | 50.7953 | 116.4918 | 25.4781 | 28.6346 | 409.6318 | 46.3375 | 8.3009 | 31.0439 | 0.8719 | -11.3635 | 9.3305 | -4.3697 | 127 | 7 | 22 | 5
612 | 2026-02-14 18:56 | 139.0225 | 9489.2895 | Phase4_UnloadCycle | 92.5426 | 8.0419 | 66.2808 | 55.1658 | 57.8025 | 50.6973 | 114.722 | 25.681 | 28.6154 | 409.7517 | 46.4372 | 8.3647 | 31.0865 | 0.8764 | -9.6145 | 9.0952 | -8.4553 | 127 | 7 | 22 | 5
613 | 2026-02-14 18:56 | 139.2497 | 9285.1779 | Phase4_UnloadCycle | 91.9786 | 7.9 | 66.3174 | 54.9785 | 57.6595 | 50.3605 | 114.8318 | 25.2684 | 28.6939 | 409.6504 | 46.4147 | 8.3478 | 31.1212 | 0.87321 | -9.5994 | 8.9824 | -5.6335 | 127 | 7 | 22 | 5
614 | 2026-02-14 18:56 | 139.4769 | 9858.4728 | Phase4_UnloadCycle | 91.4942 | 7.7572 | 66.4831 | 54.9808 | 57.4227 | 50.6046 | 114.961 | 25.4275 | 28.6128 | 409.5398 | 46.8172 | 8.3326 | 30.9779 | 0.88392 | -8.5022 | 8.6791 | -4.9043 | 127 | 7 | 22 | 5
615 | 2026-02-14 18:57 | 139.704 | 9512.0431 | Phase4_UnloadCycle | 91.6338 | 7.7514 | 66.6299 | 54.6546 | 57.1251 | 50.4705 | 116.7493 | 25.4836 | 28.7129 | 410.0003 | 46.4759 | 8.3087 | 31.0294 | 0.87563 | -8.2526 | 8.9948 | -3.5536 | 127 | 7 | 22 | 5
616 | 2026-02-14 18:57 | 139.9312 | 9524.3799 | Phase4_UnloadCycle | 91.6971 | 7.6102 | 66.6912 | 55.0829 | 57.8988 | 50.6561 | 116.5573 | 25.5025 | 28.6422 | 408.1721 | 46.5852 | 8.4098 | 31.0597 | 0.87973 | -7.0216 | 9.2315 | -3.214 | 127 | 7 | 22 | 5
617 | 2026-02-14 18:57 | 140.1583 | 9636.0969 | Phase4_UnloadCycle | 91.6059 | 7.5946 | 66.3986 | 54.9511 | 57.7645 | 50.295 | 119.0337 | 25.6198 | 28.48 | 408.1907 | 46.4981 | 8.3636 | 31.1107 | 0.88688 | -7.3853 | 8.6513 | -5.2928 | 127 | 7 | 22 | 5
618 | 2026-02-14 18:57 | 140.3855 | 9613.2974 | Phase4_UnloadCycle | 91.7681 | 7.618 | 66.2689 | 54.9354 | 58.1102 | 50.8361 | 119.9616 | 25.5572 | 28.6955 | 409.7253 | 46.5014 | 8.4304 | 31.1262 | 0.87782 | -4.6349 | 8.8983 | -3.8057 | 127 | 7 | 22 | 5
619 | 2026-02-14 18:58 | 140.6127 | 9588.566 | Phase4_UnloadCycle | 91.9374 | 7.5803 | 66.0977 | 54.9341 | 57.3518 | 50.8599 | 123.6026 | 25.3443 | 28.4452 | 409.5153 | 46.1077 | 8.3632 | 31.0952 | 0.86694 | -4.2357 | 8.4431 | -4.6297 | 127 | 7 | 22 | 5
620 | 2026-02-14 18:58 | 140.8398 | 9445.5477 | Phase4_UnloadCycle | 91.8019 | 7.6691 | 66.0924 | 54.7041 | 57.85 | 50.4665 | 125.5996 | 25.6026 | 28.7499 | 409.1132 | 46.389 | 8.3411 | 31.0886 | 0.88077 | -2.3682 | 8.5133 | 4.9675 | 127 | 7 | 22 | 5
621 | 2026-02-14 18:58 | 141.067 | 9658.1088 | Phase4_UnloadCycle | 91.7651 | 7.6605 | 66.4524 | 54.6025 | 58.1613 | 50.3868 | 125.8901 | 25.5522 | 28.6169 | 407.6184 | 46.6972 | 8.4127 | 31.078 | 0.87417 | 0.14095 | 8.4979 | 6.7385 | 127 | 7 | 22 | 5
622 | 2026-02-14 18:58 | 141.2941 | 9893.8847 | Phase4_UnloadCycle | 92.5109 | 7.7982 | 66.2721 | 55.0515 | 57.8095 | 50.6013 | 130.6855 | 25.2798 | 28.6878 | 408.3911 | 46.7088 | 8.35 | 31.0532 | 0.87853 | 2.8638 | 8.0569 | 8.7973 | 127 | 7 | 22 | 5
623 | 2026-02-14 18:59 | 141.5213 | 9825.496 | Phase4_UnloadCycle | 92.1998 | 7.9119 | 66.1029 | 54.9524 | 57.6651 | 50.7387 | 134.6278 | 25.519 | 28.8445 | 406.5077 | 46.7964 | 8.3196 | 31.0011 | 0.87311 | 4.6087 | 8.0519 | 9.6244 | 127 | 7 | 22 | 5
624 | 2026-02-14 18:59 | 141.7485 | 9879.6333 | Phase4_UnloadCycle | 91.0283 | 7.9471 | 66.0192 | 55.233 | 57.5408 | 50.6414 | 135.2482 | 25.2808 | 28.6146 | 411.2569 | 46.445 | 8.3352 | 30.9313 | 0.87343 | 6.4764 | 7.7969 | 5.0804 | 127 | 7 | 22 | 5
625 | 2026-02-14 18:59 | 141.9756 | 9566.3401 | Phase4_UnloadCycle | 90.3894 | 8.2177 | 66.5329 | 54.8777 | 57.2027 | 50.7314 | 132.099 | 25.3946 | 28.7853 | 409.5336 | 46.4357 | 8.3743 | 31.0527 | 0.87126 | 4.4235 | 8.1503 | 6.3816 | 127 | 7 | 22 | 5
626 | 2026-02-14 18:59 | 142.2028 | 9507.0451 | Phase4_UnloadCycle | 92.2862 | 8.3812 | 66.6485 | 55.2001 | 58.1493 | 50.8872 | 132.5493 | 25.3971 | 28.6091 | 410.0402 | 46.8707 | 8.3326 | 31.1262 | 0.8702 | 2.044 | 8.2049 | 7.5749 | 127 | 7 | 22 | 5
627 | 2026-02-14 19:00 | 142.4299 | 9657.4154 | Phase4_UnloadCycle | 91.0751 | 8.448 | 66.684 | 54.6491 | 57.5416 | 50.778 | 126.4484 | 25.6344 | 28.9703 | 409.3119 | 46.4607 | 8.3713 | 31.1203 | 0.85923 | 0.075337 | 8.3535 | 5.1887 | 127 | 7 | 22 | 5
628 | 2026-02-14 19:00 | 142.6571 | 9701.2032 | Phase4_UnloadCycle | 91.6839 | 8.5326 | 66.3656 | 55.5346 | 57.8404 | 50.6044 | 124.8692 | 25.5322 | 28.6352 | 408.324 | 46.6294 | 8.3897 | 30.9924 | 0.87792 | -1.4103 | 8.8199 | 2.3104 | 127 | 7 | 22 | 5
629 | 2026-02-14 19:00 | 142.8843 | 9878.8552 | Phase4_UnloadCycle | 91.1833 | 8.5692 | 66.3077 | 54.5349 | 57.2538 | 50.3675 | 123.3718 | 25.3296 | 28.6985 | 409.7763 | 46.5004 | 8.3548 | 31.0399 | 0.88618 | -3.8861 | 8.7821 | 2.0159 | 127 | 7 | 22 | 5
630 | 2026-02-14 19:00 | 143.1114 | 9458.9876 | Phase4_UnloadCycle | 90.8239 | 8.5254 | 66.0374 | 55.1795 | 57.5804 | 50.5999 | 121.9692 | 25.633 | 28.8823 | 408.6405 | 46.705 | 8.3378 | 31.0888 | 0.87792 | -4.4557 | 8.6657 | -0.89081 | 127 | 7 | 22 | 5
631 | 2026-02-14 19:01 | 143.3386 | 9977.7302 | Phase4_UnloadCycle | 92.299 | 8.5247 | 66.4553 | 54.953 | 58.3395 | 50.9626 | 119.1513 | 25.3366 | 28.6265 | 409.1509 | 46.6968 | 8.4139 | 31.0069 | 0.88168 | -6.6722 | 8.9011 | -1.9876 | 127 | 7 | 22 | 5
632 | 2026-02-14 19:01 | 143.5658 | 9729.5518 | Phase4_UnloadCycle | 92.3307 | 8.4616 | 66.2683 | 54.9815 | 57.6816 | 50.5974 | 117.5517 | 25.6605 | 28.6701 | 408.2298 | 46.6488 | 8.4219 | 31.082 | 0.87967 | -6.5692 | 8.9979 | -5.0991 | 127 | 7 | 22 | 5
633 | 2026-02-14 19:01 | 143.7929 | 9702.9852 | Phase4_UnloadCycle | 91.6521 | 8.4053 | 66.4626 | 54.9961 | 58.0907 | 50.7515 | 115.794 | 25.4887 | 28.6641 | 408.2358 | 46.1403 | 8.2811 | 31.1233 | 0.87571 | -7.5663 | 9.1178 | -2.0354 | 127 | 7 | 22 | 5
634 | 2026-02-14 19:01 | 144.0201 | 9627.0018 | Phase4_UnloadCycle | 90.7231 | 8.3185 | 65.8983 | 55.1208 | 57.667 | 50.5747 | 115.5455 | 25.5724 | 28.7475 | 410.5519 | 46.6848 | 8.435 | 31.0899 | 0.86649 | -9.8941 | 9.6858 | -6.4681 | 127 | 7 | 22 | 5
635 | 2026-02-14 19:02 | 144.2472 | 9542.0318 | Phase4_UnloadCycle | 91.5127 | 8.2273 | 66.5438 | 54.34 | 57.4041 | 50.5449 | 114.5998 | 25.6568 | 28.9297 | 410.2737 | 46.8642 | 8.4327 | 31.082 | 0.87362 | -9.4848 | 9.2753 | -9.1438 | 127 | 7 | 22 | 5
636 | 2026-02-14 19:02 | 144.4744 | 9944.5567 | Phase4_UnloadCycle | 92.1503 | 8.0118 | 66.6457 | 55.225 | 58.0301 | 50.6645 | 115.5316 | 25.518 | 28.4958 | 408.2261 | 46.7462 | 8.4061 | 31.0462 | 0.86823 | -9.624 | 8.7767 | -7.6341 | 127 | 7 | 22 | 5
637 | 2026-02-14 19:02 | 144.7016 | 9842.8566 | Phase4_UnloadCycle | 91.0342 | 7.89 | 66.4275 | 54.6324 | 57.7151 | 50.6666 | 114.48 | 25.7375 | 28.7689 | 409.9768 | 46.6497 | 8.384 | 31.0183 | 0.87161 | -10.6795 | 9.131 | -7.1392 | 127 | 7 | 22 | 5
638 | 2026-02-14 19:03 | 144.9287 | 9645.3337 | Phase4_UnloadCycle | 91.8568 | 7.8097 | 67.2263 | 54.9077 | 57.8464 | 50.5744 | 114.5017 | 25.5998 | 28.8221 | 409.1578 | 46.148 | 8.3535 | 31.0933 | 0.87655 | -9.5377 | 8.7768 | -2.8272 | 127 | 7 | 22 | 5
639 | 2026-02-14 19:03 | 145.1559 | 9659.9682 | Phase4_UnloadCycle | 92.0808 | 7.7471 | 66.4783 | 55.5885 | 57.8024 | 50.4735 | 117.7662 | 25.613 | 28.7051 | 409.7439 | 46.4623 | 8.4236 | 31.0345 | 0.8683 | -6.4913 | 9.0133 | -4.3158 | 127 | 7 | 22 | 5
640 | 2026-02-14 19:03 | 145.383 | 9825.2527 | Phase4_UnloadCycle | 92.0697 | 7.532 | 66.2549 | 55.0044 | 57.3738 | 50.673 | 117.0895 | 25.5023 | 28.9777 | 411.5122 | 46.7177 | 8.3178 | 31.2116 | 0.87846 | -7.0756 | 8.6536 | -4.4217 | 127 | 7 | 22 | 5
641 | 2026-02-14 19:03 | 145.6102 | 10153.856 | Phase4_UnloadCycle | 92.3349 | 7.5146 | 66.2794 | 54.8679 | 57.8887 | 50.8778 | 118.4392 | 25.6014 | 28.7969 | 409.5427 | 46.4617 | 8.4225 | 31.0117 | 0.86941 | -4.6471 | 8.7362 | -5.3015 | 127 | 7 | 22 | 5
642 | 2026-02-14 19:04 | 145.8374 | 9868.0227 | Phase4_UnloadCycle | 91.7557 | 7.5604 | 65.9409 | 54.8271 | 58.3578 | 50.6563 | 121.077 | 25.6327 | 28.7498 | 409.8174 | 46.8132 | 8.5116 | 30.9968 | 0.88084 | -4.0086 | 8.4712 | 1.5609 | 127 | 7 | 22 | 5
643 | 2026-02-14 19:04 | 146.0645 | 9689.2023 | Phase4_UnloadCycle | 92.2083 | 7.5347 | 66.355 | 55.4639 | 57.871 | 50.9992 | 123.387 | 25.5774 | 28.9143 | 410.3206 | 46.7691 | 8.348 | 31.021 | 0.87334 | -3.3775 | 8.7348 | -0.5169 | 127 | 7 | 22 | 5
644 | 2026-02-14 19:04 | 146.2917 | 9901.0537 | Phase4_UnloadCycle | 91.9695 | 7.6098 | 66.2976 | 54.6657 | 57.7875 | 50.918 | 123.569 | 25.4265 | 28.8042 | 409.3548 | 46.6443 | 8.4191 | 31.0362 | 0.86965 | -1.804 | 8.5298 | 2.485 | 127 | 7 | 22 | 5
645 | 2026-02-14 19:04 | 146.5188 | 9912.273 | Phase4_UnloadCycle | 91.7782 | 7.6859 | 66.894 | 54.7639 | 58.1101 | 50.6425 | 127.5327 | 25.5916 | 28.8383 | 410.7345 | 46.6181 | 8.4106 | 30.9567 | 0.87939 | 0.58864 | 8.4753 | 7.9952 | 127 | 7 | 22 | 5
646 | 2026-02-14 19:04 | 146.746 | 9549.0301 | Phase4_UnloadCycle | 91.5242 | 7.7911 | 66.6084 | 55.3766 | 57.8257 | 50.5404 | 129.0007 | 25.6352 | 28.8759 | 408.9512 | 46.5634 | 8.4116 | 31.0587 | 0.88804 | 2.5512 | 8.206 | 7.8415 | 127 | 7 | 22 | 5
647 | 2026-02-14 19:05 | 146.9732 | 9977.2615 | Phase4_UnloadCycle | 91.7276 | 7.9578 | 66.4221 | 55.4852 | 57.921 | 50.3608 | 133.9226 | 25.5805 | 28.8024 | 409.2146 | 46.3995 | 8.4259 | 31.1465 | 0.86987 | 3.9469 | 7.8063 | 4.0762 | 127 | 7 | 22 | 5
648 | 2026-02-14 19:05 | 147.2003 | 9965.1026 | Phase4_UnloadCycle | 91.0933 | 8.0212 | 66.1604 | 55.0807 | 57.5172 | 50.2926 | 135.8727 | 25.5572 | 28.8256 | 408.9911 | 46.7007 | 8.5021 | 31.0628 | 0.87375 | 5.6496 | 8.0332 | 5.779 | 127 | 7 | 22 | 5
649 | 2026-02-14 19:05 | 147.4275 | 10125.3646 | Phase4_UnloadCycle | 91.8672 | 8.2336 | 66.9505 | 54.7065 | 57.7275 | 50.4821 | 132.3896 | 25.8432 | 28.877 | 410.3096 | 46.8443 | 8.4752 | 31.1242 | 0.87256 | 6.6684 | 8.4898 | 8.0629 | 127 | 7 | 22 | 5
650 | 2026-02-14 19:05 | 147.6546 | 10320.8687 | Phase4_UnloadCycle | 93.0345 | 8.3335 | 66.6126 | 55.4561 | 58.0735 | 50.9762 | 129.15 | 25.7158 | 28.9859 | 412.6533 | 46.5642 | 8.4535 | 31.0531 | 0.87846 | 2.0902 | 8.3202 | 3.3834 | 127 | 7 | 22 | 5
651 | 2026-02-14 19:06 | 147.8818 | 10223.4584 | Phase4_UnloadCycle | 91.2751 | 8.3609 | 66.9256 | 55.1972 | 57.6483 | 50.7554 | 127.7532 | 25.5802 | 28.4568 | 409.8717 | 46.3983 | 8.3892 | 31.1908 | 0.88331 | 0.44763 | 8.2889 | 6.4135 | 127 | 7 | 22 | 5
652 | 2026-02-14 19:06 | 148.109 | 10020.9095 | Phase4_UnloadCycle | 91.4018 | 8.5583 | 66.8717 | 55.1018 | 58.2598 | 50.8186 | 125.6583 | 25.5431 | 29.022 | 409.7885 | 46.7374 | 8.482 | 31.0649 | 0.87377 | -1.3849 | 8.285 | 2.3618 | 127 | 7 | 22 | 5
653 | 2026-02-14 19:06 | 148.3361 | 9905.4967 | Phase4_UnloadCycle | 92.6217 | 8.5289 | 66.5699 | 54.7656 | 57.9025 | 50.3846 | 122.7931 | 25.5958 | 28.8062 | 411.0564 | 46.6471 | 8.5344 | 31.0857 | 0.87512 | -3.4551 | 8.501 | 1.3268 | 127 | 7 | 22 | 5
654 | 2026-02-14 19:06 | 148.5633 | 10495.7629 | Phase4_UnloadCycle | 92.1465 | 8.5947 | 66.5048 | 55.1065 | 57.9339 | 50.5801 | 120.7696 | 25.7981 | 28.6389 | 409.972 | 46.898 | 8.4698 | 31.012 | 0.86865 | -4.6821 | 8.9273 | -2.7259 | 127 | 7 | 22 | 5
655 | 2026-02-14 19:07 | 148.7905 | 10118.4646 | Phase4_UnloadCycle | 91.6257 | 8.4592 | 66.5464 | 55.2394 | 58.1723 | 50.8722 | 119.4391 | 25.6408 | 28.8994 | 410.1149 | 46.9099 | 8.4403 | 30.9524 | 0.87576 | -5.1459 | 9.1672 | 2.1434 | 127 | 7 | 22 | 5
656 | 2026-02-14 19:07 | 149.0176 | 10126.8239 | Phase4_UnloadCycle | 92.3266 | 8.4265 | 66.0253 | 55.0374 | 57.7541 | 50.9676 | 117.2912 | 25.6228 | 28.9596 | 410.835 | 46.3107 | 8.492 | 30.9902 | 0.88704 | -7.33 | 9.1306 | 3.3533 | 127 | 7 | 22 | 5
657 | 2026-02-14 19:07 | 149.2448 | 10136.3134 | Phase4_UnloadCycle | 91.7566 | 8.4656 | 66.4835 | 55.2876 | 57.979 | 50.6601 | 116.1333 | 25.7489 | 29.0411 | 409.7327 | 46.4721 | 8.4863 | 31.008 | 0.87935 | -9.0956 | 9.3664 | -6.1794 | 127 | 7 | 22 | 5
658 | 2026-02-14 19:08 | 149.4719 | 10186.4586 | Phase4_UnloadCycle | 93.2036 | 8.3607 | 66.8087 | 55.164 | 57.6362 | 50.9789 | 114.484 | 25.6434 | 28.5633 | 410.635 | 46.6456 | 8.5375 | 31.0427 | 0.86644 | -8.5897 | 9.3464 | -4.5346 | 127 | 7 | 22 | 5
659 | 2026-02-14 19:08 | 149.6991 | 10148.3994 | Phase4_UnloadCycle | 92.3845 | 8.2147 | 66.5287 | 54.8614 | 57.931 | 51.1223 | 116.164 | 25.8892 | 29.1553 | 411.3965 | 46.9847 | 8.4254 | 31.0278 | 0.87288 | -9.4779 | 9.3944 | -6.2884 | 127 | 7 | 22 | 5
660 | 2026-02-14 19:08 | 149.9263 | 10096.7724 | Phase4_UnloadCycle | 91.7902 | 8.0732 | 66.2307 | 55.4737 | 57.9653 | 50.6534 | 115.3048 | 25.8493 | 28.8768 | 411.6368 | 46.4599 | 8.4776 | 30.9711 | 0.87415 | -8.4688 | 9.1782 | -7.4707 | 127 | 7 | 22 | 5
661 | 2026-02-14 19:08 | 150.1534 | 10116.3932 | Phase4_UnloadCycle | 93.1563 | 8.0132 | 66.4963 | 55.2056 | 57.9801 | 50.7433 | 114.7493 | 25.6589 | 28.9735 | 410.6938 | 47.0327 | 8.484 | 30.9439 | 0.87452 | -8.3681 | 9.2951 | -8.2507 | 127 | 7 | 22 | 5
662 | 2026-02-14 19:08 | 150.3806 | 10212.1352 | Phase4_UnloadCycle | 91.3818 | 7.7522 | 67.1109 | 55.5588 | 57.5331 | 50.8499 | 117.5621 | 25.67 | 29.0748 | 413.5737 | 46.7983 | 8.4384 | 31.0516 | 0.87908 | -8.6085 | 9.0701 | -8.6905 | 127 | 7 | 22 | 5
663 | 2026-02-14 19:09 | 150.6077 | 10147.7975 | Phase4_UnloadCycle | 92.7237 | 7.7107 | 67.004 | 55.4868 | 57.6128 | 51.1377 | 116.5813 | 25.4565 | 28.8518 | 410.016 | 46.7068 | 8.4483 | 30.9783 | 0.88276 | -9.1019 | 9.2037 | -8.2569 | 127 | 7 | 22 | 5
664 | 2026-02-14 19:09 | 150.8349 | 10136.7662 | Phase4_UnloadCycle | 92.4817 | 7.5274 | 66.5649 | 54.8974 | 58.07 | 50.3034 | 116.7228 | 25.5406 | 29.1056 | 411.0313 | 46.7946 | 8.5242 | 31.0921 | 0.88778 | -8.2174 | 9.2026 | -3.4875 | 127 | 7 | 22 | 5
665 | 2026-02-14 19:09 | 151.0621 | 10280.1787 | Phase4_UnloadCycle | 92.9498 | 7.5962 | 66.742 | 55.127 | 57.879 | 50.8824 | 119.7 | 25.638 | 28.9797 | 410.4267 | 46.5458 | 8.4591 | 31.1046 | 0.87765 | -6.3017 | 9.3788 | -4.5872 | 127 | 7 | 22 | 5
666 | 2026-02-14 19:10 | 151.2892 | 10239.1574 | Phase4_UnloadCycle | 92.9325 | 7.5408 | 66.3574 | 54.9842 | 57.8789 | 50.6745 | 121.5638 | 25.8373 | 28.7076 | 410.3037 | 46.8102 | 8.4717 | 31.108 | 0.8847 | -4.3207 | 8.5888 | -7.6289 | 127 | 7 | 22 | 5
667 | 2026-02-14 19:10 | 151.5164 | 10529.3588 | Phase4_UnloadCycle | 92.0949 | 7.6373 | 66.1516 | 54.7724 | 57.6749 | 50.8663 | 123.4351 | 25.7105 | 29.1216 | 411.449 | 46.7278 | 8.4979 | 31.0372 | 0.87329 | -3.3123 | 8.8233 | 1.7742 | 127 | 7 | 22 | 5
668 | 2026-02-14 19:10 | 151.7435 | 9895.7489 | Phase4_UnloadCycle | 91.6316 | 7.6021 | 66.3258 | 55.0529 | 57.6868 | 50.5178 | 125.0864 | 25.7066 | 28.9538 | 410.6861 | 46.7235 | 8.5327 | 31.1073 | 0.87556 | -1.5428 | 8.8961 | 2.2025 | 127 | 7 | 22 | 5
669 | 2026-02-14 19:10 | 151.9707 | 10495.7925 | Phase4_UnloadCycle | 92.5555 | 7.7475 | 66.6907 | 55.5871 | 57.4986 | 50.8326 | 128.0018 | 25.7287 | 29.0136 | 412.6918 | 46.4923 | 8.4787 | 31.1071 | 0.89298 | 0.10294 | 8.626 | 7.2802 | 127 | 7 | 22 | 5
670 | 2026-02-14 19:10 | 152.1979 | 10535.3729 | Phase4_UnloadCycle | 91.8589 | 7.7628 | 66.3517 | 54.7441 | 58.0216 | 50.7673 | 130.1564 | 25.8512 | 28.9853 | 411.7739 | 46.5195 | 8.5535 | 31.1525 | 0.87105 | 2.6421 | 8.4453 | 7.249 | 127 | 7 | 22 | 5
671 | 2026-02-14 19:11 | 152.425 | 10032.2739 | Phase4_UnloadCycle | 92.9699 | 7.9514 | 66.4518 | 55.1619 | 57.8467 | 51.3541 | 133.2115 | 25.7897 | 29.1009 | 413.074 | 47.2414 | 8.4598 | 31.1015 | 0.87614 | 2.9589 | 8.2602 | 4.2074 | 127 | 7 | 22 | 5
672 | 2026-02-14 19:11 | 152.6522 | 10318.0597 | Phase4_UnloadCycle | 92.1055 | 8.0778 | 66.3871 | 55.2092 | 57.7087 | 50.95 | 133.5929 | 25.6481 | 28.9949 | 412.3979 | 46.9042 | 8.4379 | 31.0625 | 0.86648 | 5.7191 | 8.2484 | 4.2644 | 127 | 7 | 22 | 5
673 | 2026-02-14 19:11 | 152.8794 | 10329.0021 | Phase4_UnloadCycle | 91.9758 | 8.2132 | 67.1587 | 55.2352 | 57.7856 | 50.6169 | 131.9068 | 25.8885 | 29.2859 | 412.4307 | 47.0724 | 8.5737 | 31.0074 | 0.87295 | 3.7367 | 7.9866 | 5.3066 | 127 | 7 | 22 | 5
674 | 2026-02-14 19:12 | 153.1065 | 10182.5921 | Phase4_UnloadCycle | 92.1355 | 8.3309 | 66.9497 | 55.0928 | 58.1017 | 50.7367 | 131.3805 | 25.7073 | 28.9299 | 412.9845 | 47.1733 | 8.4588 | 31.0313 | 0.87002 | 3.1106 | 8.0377 | 4.161 | 127 | 7 | 22 | 5
675 | 2026-02-14 19:12 | 153.3337 | 10296.3902 | Phase4_UnloadCycle | 91.5357 | 8.3574 | 67.09 | 54.8379 | 58.4483 | 50.8443 | 126.8088 | 25.9709 | 28.9502 | 413.5391 | 46.5411 | 8.5818 | 30.9697 | 0.88335 | -0.18139 | 8.4622 | 6.4187 | 127 | 7 | 22 | 5
676 | 2026-02-14 19:12 | 153.5608 | 10259.8441 | Phase4_UnloadCycle | 91.9376 | 8.4434 | 66.7906 | 55.2441 | 57.4981 | 50.4714 | 124.5007 | 25.9382 | 29.1042 | 412.929 | 47.2198 | 8.5237 | 31.0461 | 0.88657 | -1.4519 | 8.2017 | 1.7365 | 127 | 7 | 22 | 5
677 | 2026-02-14 19:12 | 153.788 | 10722.4812 | Phase4_UnloadCycle | 93.0744 | 8.5184 | 66.5643 | 55.0224 | 58.3775 | 50.8473 | 122.9345 | 25.7963 | 29.4408 | 413.1465 | 46.3962 | 8.5754 | 30.9842 | 0.87638 | -2.7578 | 9.0342 | 2.9642 | 127 | 7 | 22 | 5
678 | 2026-02-14 19:12 | 154.0152 | 10610.3558 | Phase4_UnloadCycle | 91.9223 | 8.6561 | 66.18 | 55.0664 | 58.2888 | 50.9184 | 120.0422 | 25.8474 | 29.1634 | 414.0251 | 46.7047 | 8.5997 | 31.1012 | 0.88523 | -3.8267 | 9.1868 | -5.2384 | 127 | 7 | 22 | 5
679 | 2026-02-14 19:13 | 154.2423 | 10678.2568 | Phase4_UnloadCycle | 91.4907 | 8.5825 | 66.9148 | 55.3366 | 57.8804 | 50.58 | 117.5293 | 25.8355 | 29.3025 | 412.6629 | 46.831 | 8.5602 | 31.0018 | 0.87866 | -5.1751 | 8.9652 | -0.83337 | 127 | 7 | 22 | 5
680 | 2026-02-14 19:13 | 154.4695 | 10607.7939 | Phase4_UnloadCycle | 92.6053 | 8.5043 | 66.2396 | 55.4763 | 57.9985 | 51.0619 | 117.7358 | 25.6582 | 29.1451 | 413.3519 | 47.0414 | 8.5876 | 31.0704 | 0.87625 | -7.1811 | 9.08 | -2.7161 | 127 | 7 | 22 | 5
681 | 2026-02-14 19:13 | 154.6966 | 10334.1275 | Phase4_UnloadCycle | 92.6226 | 8.4005 | 66.5828 | 55.2066 | 57.9352 | 50.7748 | 116.6879 | 25.9398 | 29.0213 | 414.2982 | 46.8603 | 8.6154 | 31.0562 | 0.87511 | -8.522 | 9.2279 | -10.7918 | 127 | 7 | 22 | 5
682 | 2026-02-14 19:14 | 154.9238 | 10443.9949 | Phase4_UnloadCycle | 92.5001 | 8.3029 | 66.3123 | 55.5086 | 58.1989 | 50.6616 | 116.0139 | 25.9018 | 29.1008 | 414.0353 | 46.9172 | 8.6508 | 31.0506 | 0.85784 | -9.052 | 9.309 | -2.925 | 127 | 7 | 22 | 5
683 | 2026-02-14 19:14 | 155.151 | 10617.8086 | Phase4_UnloadCycle | 92.6258 | 8.2069 | 66.4687 | 55.4964 | 58.3958 | 50.8098 | 115.0836 | 26.0337 | 29.1807 | 414.2215 | 46.8919 | 8.5387 | 31.0503 | 0.87314 | -9.4463 | 9.4136 | -7.168 | 127 | 7 | 22 | 5
684 | 2026-02-14 19:14 | 155.3781 | 10365.8899 | Phase4_UnloadCycle | 91.792 | 7.9537 | 66.5097 | 55.1828 | 58.2319 | 51.2176 | 115.3098 | 25.9159 | 29.3122 | 414.6146 | 46.6979 | 8.6771 | 30.9914 | 0.874 | -9.5183 | 9.5066 | -6.4481 | 127 | 7 | 22 | 5
685 | 2026-02-14 19:14 | 155.6053 | 10683.6086 | Phase4_UnloadCycle | 91.5393 | 7.9922 | 66.365 | 55.4504 | 58.1926 | 50.9837 | 116.3621 | 25.9324 | 29.4028 | 414.5764 | 46.5544 | 8.5892 | 31.0651 | 0.86929 | -8.6852 | 9.3358 | -9.3872 | 127 | 7 | 22 | 5
686 | 2026-02-14 19:14 | 155.8324 | 10550.1244 | Phase4_UnloadCycle | 93.1851 | 7.8285 | 66.6035 | 54.9785 | 58.1421 | 50.9008 | 115.6244 | 25.7193 | 29.2917 | 416.1868 | 47.0335 | 8.6596 | 30.9907 | 0.87593 | -8.556 | 9.5502 | -3.7197 | 127 | 7 | 22 | 5
687 | 2026-02-14 19:15 | 156.0596 | 10544.5489 | Phase4_UnloadCycle | 92.1322 | 7.7339 | 66.1858 | 55.4547 | 57.4968 | 50.733 | 115.9783 | 25.8157 | 29.43 | 415.7589 | 47.0755 | 8.6216 | 31.0153 | 0.8607 | -7.9125 | 9.4056 | -9.4679 | 127 | 7 | 22 | 5
688 | 2026-02-14 19:15 | 156.2868 | 10729.5919 | Phase4_UnloadCycle | 91.8871 | 7.6122 | 66.9762 | 55.3707 | 58.1603 | 50.7098 | 117.5142 | 25.8607 | 29.0707 | 414.8395 | 47.1929 | 8.5585 | 31.0373 | 0.86998 | -6.4568 | 9.0673 | -2.7651 | 127 | 7 | 22 | 5
689 | 2026-02-14 19:15 | 156.5139 | 10703.3653 | Phase4_UnloadCycle | 93.0603 | 7.5867 | 66.1606 | 55.3946 | 58.2609 | 50.7931 | 119.7609 | 26.093 | 29.1608 | 415.5838 | 46.732 | 8.5745 | 31.1145 | 0.8756 | -4.8562 | 9.3574 | -1.4313 | 127 | 7 | 22 | 5
690 | 2026-02-14 19:16 | 156.7411 | 10593.0149 | Phase4_UnloadCycle | 92.697 | 7.5661 | 66.6186 | 55.0426 | 57.7622 | 50.4693 | 122.1482 | 25.9837 | 29.1478 | 416.1817 | 47.0833 | 8.6119 | 31.0669 | 0.8709 | -4.6661 | 8.6907 | -4.5802 | 127 | 7 | 22 | 5
691 | 2026-02-14 19:16 | 156.9682 | 10845.9332 | Phase4_UnloadCycle | 92.6622 | 7.6418 | 67.1033 | 55.2817 | 57.793 | 51.0893 | 122.2827 | 26.0683 | 29.3885 | 415.6097 | 46.871 | 8.6262 | 30.9783 | 0.87737 | -2.5784 | 8.8515 | 4.2321 | 127 | 7 | 22 | 5
692 | 2026-02-14 19:16 | 157.1954 | 10511.3968 | Phase4_UnloadCycle | 93.3361 | 7.5749 | 66.6961 | 55.1879 | 57.9351 | 50.7904 | 125.1049 | 26.0678 | 29.2777 | 415.8011 | 47.0262 | 8.6758 | 31.0571 | 0.87733 | -1.7885 | 8.9106 | 1.7371 | 127 | 7 | 22 | 5
693 | 2026-02-14 19:16 | 157.4226 | 10791.9178 | Phase4_UnloadCycle | 91.9619 | 7.7271 | 66.4981 | 55.025 | 58.0264 | 50.8256 | 128.3564 | 25.9763 | 29.4372 | 415.5241 | 47.1732 | 8.6756 | 31.1576 | 0.87036 | 1.6245 | 8.3687 | 5.2676 | 127 | 7 | 22 | 5
694 | 2026-02-14 19:16 | 157.6497 | 10803.7847 | Phase4_UnloadCycle | 92.7512 | 7.7896 | 66.6827 | 55.1452 | 57.7225 | 50.7165 | 129.5185 | 26.0731 | 29.1827 | 415.1728 | 46.7156 | 8.6696 | 31.1116 | 0.8644 | 3.3331 | 8.4274 | 1.6129 | 127 | 7 | 22 | 5
695 | 2026-02-14 19:17 | 157.8769 | 10678.2167 | Phase4_UnloadCycle | 92.5084 | 7.9872 | 66.9139 | 55.1319 | 58.0199 | 50.8093 | 132.9008 | 26.2 | 29.3341 | 416.8939 | 46.747 | 8.6446 | 31.0752 | 0.86887 | 5.296 | 8.3284 | 12.7832 | 127 | 7 | 22 | 5
696 | 2026-02-14 19:17 | 158.1041 | 10792.9496 | Phase4_UnloadCycle | 92.219 | 8.0166 | 66.982 | 55.6735 | 57.6848 | 50.8055 | 134.0169 | 26.0256 | 29.4567 | 417.7263 | 46.9451 | 8.6797 | 31.1066 | 0.87251 | 6.5508 | 7.9135 | 5.834 | 127 | 7 | 22 | 5
697 | 2026-02-14 19:17 | 158.3312 | 10562.003 | Phase4_UnloadCycle | 93.0971 | 8.118 | 66.256 | 55.5349 | 57.9291 | 50.509 | 131.3573 | 26.2097 | 29.0707 | 417.062 | 47.0662 | 8.6646 | 31.082 | 0.87165 | 4.1544 | 8.2096 | 9.923 | 127 | 7 | 22 | 5
698 | 2026-02-14 19:18 | 158.5584 | 10917.2141 | Phase4_UnloadCycle | 92.8524 | 8.254 | 66.9245 | 55.7739 | 58.2965 | 51.1978 | 130.3127 | 26.0031 | 29.6245 | 415.7615 | 46.809 | 8.6684 | 30.9122 | 0.86424 | 1.4509 | 8.3673 | 2.589 | 127 | 7 | 22 | 5
699 | 2026-02-14 19:18 | 158.7855 | 10759.4229 | Phase4_UnloadCycle | 92.6067 | 8.4378 | 66.2188 | 55.1097 | 58.0532 | 50.6295 | 127.5254 | 26.1202 | 29.3776 | 417.9695 | 46.6982 | 8.6849 | 31.1133 | 0.8778 | 0.6401 | 8.4426 | 1.6143 | 127 | 7 | 22 | 5
700 | 2026-02-14 19:18 | 159.0127 | 10722.0861 | Phase4_UnloadCycle | 93.1741 | 8.4473 | 66.8668 | 55.3527 | 57.755 | 50.7181 | 125.2377 | 26.2362 | 29.1366 | 418.0042 | 46.8766 | 8.6367 | 31.1288 | 0.86934 | -0.51298 | 9.2079 | 2.9803 | 127 | 7 | 22 | 5
701 | 2026-02-14 19:18 | 159.2399 | 10983.0392 | Phase4_UnloadCycle | 92.3575 | 8.5369 | 66.8882 | 55.193 | 58.0079 | 50.7122 | 123.2311 | 26.0628 | 29.4533 | 416.4389 | 47.0642 | 8.7312 | 31.1624 | 0.87 | -3.1596 | 8.7143 | 1.9243 | 127 | 7 | 22 | 5
702 | 2026-02-14 19:19 | 159.467 | 10724.5831 | Phase4_UnloadCycle | 91.7171 | 8.5933 | 66.4727 | 55.3707 | 58.3731 | 51.125 | 120.4652 | 26.237 | 29.5287 | 417.7793 | 47.0758 | 8.5959 | 31.1153 | 0.85745 | -3.987 | 9.2437 | -6.0239 | 127 | 7 | 22 | 5
703 | 2026-02-14 19:19 | 159.6942 | 10630.0273 | Phase4_UnloadCycle | 91.7775 | 8.6273 | 66.5667 | 55.271 | 57.9988 | 50.8764 | 119.451 | 26.2175 | 29.5098 | 417.9892 | 46.8445 | 8.7221 | 31.1082 | 0.87815 | -5.3595 | 9.0879 | -1.5996 | 127 | 7 | 22 | 5
704 | 2026-02-14 19:19 | 159.9213 | 10622.316 | Phase4_UnloadCycle | 91.7324 | 8.4556 | 66.4864 | 55.5198 | 57.9885 | 50.4815 | 116.8799 | 26.3446 | 29.5854 | 419.1468 | 46.7777 | 8.8103 | 30.9728 | 0.87066 | -7.3449 | 9.0458 | -2.9508 | 127 | 7 | 22 | 5
705 | 2026-02-14 19:19 | 160.1485 | 10975.5743 | Phase4_UnloadCycle | 93.2923 | 8.3417 | 66.8177 | 55.2265 | 58.1722 | 51.0339 | 118.1037 | 25.9847 | 29.6042 | 419.5324 | 47.1185 | 8.7194 | 31.0763 | 0.87128 | -7.0543 | 9.3801 | -9.1379 | 127 | 7 | 22 | 5
706 | 2026-02-14 19:20 | 160.3757 | 10696.3288 | Phase4_UnloadCycle | 91.8285 | 8.3039 | 67.1097 | 55.4997 | 58.0126 | 50.9348 | 114.8639 | 26.0098 | 29.5621 | 420.4624 | 46.6068 | 8.7271 | 31.0671 | 0.8683 | -10.5769 | 9.5721 | -3.6324 | 127 | 7 | 22 | 5
707 | 2026-02-14 19:20 | 160.6028 | 11185.8929 | Phase4_UnloadCycle | 92.4089 | 8.1443 | 66.6586 | 55.582 | 58.2748 | 50.8128 | 116.0798 | 26.3111 | 29.5721 | 419.8528 | 47.124 | 8.7341 | 31.2383 | 0.8666 | -9.2738 | 9.6058 | -11.16 | 127 | 7 | 22 | 5
708 | 2026-02-14 19:20 | 160.83 | 10601.9949 | Phase4_UnloadCycle | 92.4185 | 8.0318 | 66.8651 | 55.9388 | 58.2883 | 50.8023 | 114.1677 | 26.4437 | 29.566 | 421.1877 | 46.8711 | 8.8126 | 31.0234 | 0.87549 | -10.0211 | 9.8545 | -10.4785 | 127 | 7 | 22 | 5
709 | 2026-02-14 19:20 | 161.0571 | 11207.6478 | Phase4_UnloadCycle | 92.946 | 8.0204 | 65.9999 | 55.1162 | 57.9994 | 51.336 | 116.1864 | 26.1302 | 29.7965 | 419.8404 | 47.2798 | 8.7637 | 31.1531 | 0.86101 | -9.4282 | 10.0802 | -6.92 | 127 | 7 | 22 | 5
710 | 2026-02-14 19:20 | 161.2843 | 10991.0423 | Phase4_UnloadCycle | 92.831 | 7.8187 | 66.5733 | 55.6079 | 58.4492 | 51.0932 | 116.0526 | 26.2537 | 29.3642 | 420.743 | 46.8474 | 8.7082 | 31.2033 | 0.86508 | -8.1814 | 9.4771 | -9.6836 | 127 | 7 | 22 | 5
711 | 2026-02-14 19:21 | 161.5115 | 10958.4059 | Phase4_UnloadCycle | 93.0357 | 7.7237 | 66.652 | 55.6455 | 58.0433 | 50.5185 | 116.5883 | 26.3436 | 29.6559 | 420.978 | 47.2112 | 8.8093 | 31.2078 | 0.86165 | -7.667 | 9.2609 | -6.4503 | 127 | 7 | 22 | 5
712 | 2026-02-14 19:21 | 161.7386 | 10903.8258 | Phase4_UnloadCycle | 92.3959 | 7.5881 | 66.2232 | 55.0762 | 58.6897 | 51.0204 | 118.8328 | 26.471 | 29.5947 | 421.0445 | 46.7518 | 8.7889 | 31.1524 | 0.86763 | -6.7328 | 9.3899 | -5.2493 | 127 | 7 | 22 | 5
713 | 2026-02-14 19:21 | 161.9658 | 11066.73 | Phase4_UnloadCycle | 92.4658 | 7.5195 | 66.4096 | 55.6015 | 58.0358 | 50.8412 | 119.6871 | 26.0944 | 29.7051 | 420.797 | 47.051 | 8.769 | 31.1558 | 0.86416 | -5.3862 | 9.1307 | -4.9364 | 127 | 7 | 22 | 5
714 | 2026-02-14 19:21 | 162.193 | 11013.9362 | Phase4_UnloadCycle | 92.6273 | 7.5224 | 66.4936 | 55.2927 | 58.1082 | 50.8616 | 121.7822 | 26.2579 | 29.5994 | 421.3521 | 46.691 | 8.7911 | 31.0897 | 0.85874 | -5.0728 | 9.2846 | -1.1845 | 127 | 7 | 22 | 5
715 | 2026-02-14 19:22 | 162.4201 | 11207.595 | Phase4_UnloadCycle | 92.4332 | 7.5398 | 66.6031 | 55.3917 | 58.0913 | 50.728 | 122.2955 | 26.3651 | 29.4572 | 422.7403 | 46.5184 | 8.8907 | 31.0892 | 0.86856 | -3.8602 | 8.6961 | -2.2278 | 127 | 7 | 22 | 5
716 | 2026-02-14 19:22 | 162.6473 | 11068.5264 | Phase4_UnloadCycle | 93.3026 | 7.7023 | 66.5621 | 55.2064 | 58.027 | 50.7791 | 124.0212 | 26.4931 | 29.694 | 421.7539 | 47.0977 | 8.8456 | 31.095 | 0.86202 | -1.161 | 9.301 | 0.79171 | 127 | 7 | 22 | 5
717 | 2026-02-14 19:22 | 162.8744 | 11089.5954 | Phase4_UnloadCycle | 92.9181 | 7.7255 | 65.8308 | 55.3493 | 58.4537 | 50.7476 | 127.7441 | 26.7576 | 29.7941 | 421.7529 | 46.9871 | 8.875 | 31.1407 | 0.86267 | 0.10098 | 8.8509 | 4.8941 | 127 | 7 | 22 | 5
718 | 2026-02-14 19:22 | 163.1016 | 11024.7512 | Phase4_UnloadCycle | 93.2274 | 7.7926 | 66.0596 | 55.8548 | 58.1655 | 50.9101 | 129.6881 | 26.4876 | 29.8943 | 422.1996 | 46.7332 | 8.8031 | 31.0292 | 0.86092 | 1.2937 | 8.1667 | 6.0372 | 127 | 7 | 22 | 5
719 | 2026-02-14 19:23 | 163.3288 | 11088.0892 | Phase4_UnloadCycle | 92.9654 | 7.9518 | 66.389 | 55.4892 | 58.0771 | 51.0863 | 133.4852 | 26.3303 | 29.5904 | 424.2845 | 46.8465 | 8.8175 | 31.1434 | 0.85615 | 5.3335 | 8.1967 | 8.1573 | 127 | 7 | 22 | 5
720 | 2026-02-14 19:23 | 163.5559 | 11160.5001 | Phase4_UnloadCycle | 93.4276 | 8.0884 | 66.597 | 55.6856 | 58.3217 | 50.4768 | 135.2819 | 26.5012 | 29.9228 | 423.6416 | 47.0553 | 8.8463 | 31.151 | 0.85488 | 7.4909 | 8.3726 | 4.9293 | 127 | 7 | 22 | 5